SPECIFICATION: BLUEBOX LIGHTING CONTROL SYSTEM

1. LIGHTING CONTROL SYSTEM TO BE MANUFACTURED BY LIGHTING CONTROL & DESIGN, GLENDALE, CA (800) 345-4448.

2. LIGHTING CONTROL SYSTEM SHALL BE DIGITAL AND CONSIST OF A MASTER LCP WITH UP TO 16 INDIVIDUAL RELAYS, REMOTE LCPS WITH UP TO 16 INDIVIDUAL RELAYS IN EACH PANEL, DIGITAL SWITCHES AND DIGITAL INTERFACE CARDS. ALL SYSTEM COMPONENTS SHALL CONNECT IN A "DAISY CHAIN" STYLE CONFIGURATION AND BE CONTROLLED VIA CATEGORY 5 PATCH CABLE WITH RJ45 CONNECTORS, PROVIDING REAL-TIME TWO-WAY COMMUNICATION WITH EACH SYSTEM COMPONENT. ANALOG SYSTEMS ARE NOT ACCEPTABLE. ALL CABLES SUPPLIED BY CONTRACTOR.

3. RELAY PANELS SHALL BE PRE-WIRED, PRE-ASSEMBLED, PREPROGRAMMED AND LISTED TO UL 916 (NORMAL) OR ETL LISTED TO UL924 (EMERGENCY). PANELS SHALL BE PROVIDED WITH DUAL VOLTAGE POWER SUPPLY.

4. STANDARD RELAYS SHALL HAVE NORMALLY CLOSED LATCHING (NCL) CONTACTS UL LISTED 30A AT 277VAC AND 20A AT 347VAC FOR BALLAST/HID AND 20A TUNGSTEN AT 120VAC WITH AN 18,000A SCCR AT 277VAC. 250,000 OPERATONS AT 30AMP FULLY LOADED.  NO EXCEPTIONS. OPTIONAL 480VAC 2-POLE RELAY SHALL BE AVAILABLE.

5. RELAY PANEL ELECTRONICS SHALL PROVIDE CURRENT VISUAL STATUS AND CONTROL OF EACH RELAY OR ZONE. ALL SYSTEM CONTROL ELECTRONICS SHALL STORE PROGRAMMING IN A NON-VOLATILE MEMORY AND PROVIDE 10 YEAR BATTERY BACK UP FOR TIME OF DAY.

6. LIGHTING CONTROL SYSTEM SHALL CONSIST OF MASTER AND REMOTE PANEL(S) CONTROLLED BY A 32-CHANNEL DIGITAL TIME CLOCK (DTC) THAT CONTROLS AND PROGRAMS THE ENTIRE LIGHTING CONTROL SYSTEM.  THE DTC SHALL SUPPLY ALL TIME FUNCTIONS AND ACCEPT OTHER INPUTS. THE DTC SHALL ACCEPT CONTROL LOCALLY USING BUILT IN BUTTON PROMPTS AND USE OF AN 8 LINE 21-LETTER DISPLAY, FROM A COMPUTER, MODEM, ETHERNET OR INTERNET. ALL COMMANDS SHALL BE IN PLAIN ENGLISH. HELP PAGES SHALL DISPLAY ON THE DTC SCREEN.

7. ALL SWITCHES SHALL COMMUNICATE VIA RS 485, CAT 5 PATCH CABLE WITH RJ45 CONNECTORS. CONTACT CLOSURE STYLE SWITCHES ARE NOT ACCEPTABLE.  ANY SWITCH BUTTON FUNCTION SHALL BE ABLE TO BE CHANGED LOCALLY (AT THE DTC OR A PC) OR REMOTELY, VIA MODEM, ETHERNET OR INTERNET.  REFER TO SINGLE LINE DIAGRAM FOR WIRING DETAILS. SWITCHES WHICH CANNOT BE PROGRAMMED REMOTELY SHALL NOT BE ACCEPTABLE.

8. PHOTOCELL, EXTERIOR (PCO) OR INTERIOR (PCI), SHALL PROVIDE READOUT ON THE DTC SCREEN IN NUMBER VALUES ANALOGOUS TO FOOT-CANDLES. EACH PHOTOCELL SHALL PROVIDE A MINIMUM OF 14 TRIGGER POINTS. EACH TRIGGER CAN BE PROGRAMMED TO CONTROL ANY RELAY OR ZONE. EACH TRIGGER SHALL BE SET THROUGH DTC, LOCALLY OR REMOTELY. PHOTOCELLS THAT REQUIRE THE USE OF SET SCREWS OR MANUAL ADJUSTMENTS AT THE PHOTOCELL CONTROL CARD SHALL NOT BE ACCEPTABLE.

9. LIGHTING CONTROL SYSTEM INTERFACES TO INCLUDE A DRY CONTACT INPUT INTERFACE, BMS INTERFACE, DIMMING SYSTEM INTERFACE, ETHERNET/INTERNET INTERFACE AND AN INTERFACE TO SMARTBREAKER PANEL BOARDS. VERIFY AND INSTALL ONLY THOSE INTERFACES INDICATED ON THE PLANS.

10. STANDARD LIGHTING CONTROL SYSTEM SOFTWARE, PRE-INSTALLED INTO THE DTC, SHALL CONSIST OF AND USE STANDARD GRAPHICAL MANAGEMENT SOFTWARE (GMS) PAGES. GMS SOFTWARE SHALL PROVIDE VIA LOCAL OR REMOTE PC A VISUAL REPRESENTATION OF EACH DEVICE ON THE BUS, SHOW REAL TIME STATUS AND THE ABILITY TO CHANGE THE STATUS OF ANY INDIVIDUAL DEVICE, RELAY OR ZONE. OPTIONAL SOFTWARE THAT ACCEPTS JOB SPECIFIC GRAPHICS SHALL BE AVAILABLE. NO EXCEPTIONS.

11. START UP: EC SHALL CONTACT LC&D AT LEAST 7 DAYS BEFORE TURNOVER OF PROJECT. LC&D WILL REMOTELY DIAL INTO THE LIGHTING CONTROL SYSTEM, RUN DIAGNOSTICS AND CONFIRM SYSTEM PROGRAMMING.  EC SHALL BE AVAILABLE AT THE TIME OF DIAL IN TO PERFORM ANY CORRECTIONS REQUIRED BY LC&D. EC IS RESPONSIBLE FOR COORDINATING WITH GC AND THE OWNER, THE INSTALLATION OF A DEDICATED TELEPHONE LINE OR A SHARED PHONE LINE WITH A/B SWITCH. PHONE JACK SHALL BE MOUNTED WITHIN 12" OF MASTER LCP. LABEL JACK WITH PHONE NUMBER.  EC SHALL CONNECT PHONE LINE FROM JACK TO MASTER LCP. NO EXCEPTIONS.

12. TELEPHONE FACTORY DIAL-UP SUPPORT SHALL BE AVAILABLE AT NO ADDITIONAL COST TO THE EC OR OWNER BOTH DURING AND AFTER THE 3 YEAR WARRANTY PERIOD. FACTORY SHALL PREPROGRAM THE LIGHTING CONTROL SYSTEM PER PLANS AND APPROVED SUBMITTAL. THE LIGHTING CONTROL MANUFACTURER, AT NO ADDED COST, SHALL PROVIDE ADDITIONAL PROGRAMMING VIA MODEM AS REQUIRED BY THE EC OR OWNER FOR THE OPERATIONAL LIFE OF THE SYSTEM.  MANUFACTURER WARRANTS THAT THE DTC SOFTWARE CAN BE UPGRADED AND MONITORED REMOTELY. NO EXCEPTIONS.

13. SHOP DRAWINGS: SUBMIT DRAWINGS OF LIGHTING CONTROL SYSTEM AND ACCESSORIES INCLUDING, BUT NOT NECESSARILY LIMITED TO, RELAY PANELS, SWITCHES, DTC, PHOTOCELLS AND OTHER INTERFACES.  DRAWINGS SHALL INDICATE EXACT LOCATION AND PROGRAMMING OF EACH DEVICE. INDICATE ALL TIME SCHEDULES AND SWITCH BUTTON ENGRAVING.