# SECTION 260926

# LIGHTING CONTROL PANELBOARDS

- GENERAL

SUMMARY

Section Includes:

Lighting control systems.

Related Sections:

Section 262726 - Wiring Devices

Section 260923 – Lighting Control Devices: Occupancy sensors used in conjunction with lighting control system.

REFERENCES

American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE):

C62.41-1991 – Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

ASTM International (ASTM):

D4674 -02a Standard Test Method for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Fluorescent Lighting and Window-Filtered Daylight.

International Organization for Standardization (ISO):

9001:2000 – Quality Management Systems.

National Electrical Manufacturers Association (NEMA):

WD1 (R2005) - General Color Requirements for Wiring Devices.

Underwriters Laboratories, Inc. (UL):

489 (2002) - Molded-Case Circuit Breakers, Molded-Case Switches, and Circuit-Breaker Enclosures.

508 (1999) - Standard for Industrial Control Equipment.

924 (2003) - Emergency Lighting and Power Equipment

SYSTEM DESCRIPTION

Lighting Control System

Factory assembled switching panels, interfaces and modules.

Low voltage wall stations, control interfaces and sensors.

SUBMITTALS

Submit under provisions of Section 013300.

Specification Conformance Document:  Indicate whether the submitted equipment either:

Meets specification exactly as stated.

Meets specification via an alternate means and indicate the specific methodology used.

Shop Drawings; include:

Load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, circuits that are on emergency, and capacity, phase, and corresponding circuit numbers.

Schematic of system.

Product Data: Catalog cut sheets with performance specifications demonstrating compliance with specified requirements.

CLOSEOUT SUBMITTALS

Sustainable Design Closeout Documentation (LSC-LEED-DOC)

Lighting Control System Manufacturer to provide Enhanced Startup documentation that details the start-up procedure being performed including a process to follow, details on tests performed and an area that documents any test results.

QUALITY ASSURANCE

Manufacturer: Minimum 10 years of experience in manufacture of architectural lighting controls.

Manufacturer’s Quality System: Registered to ISO 9001:2000 Quality Standards, including in-house engineering for product design activities.

Architectural Lighting Control System:

Listed by UL specifically for the required loads. Provide evidence of compliance upon request.

PROJECT CONDITIONS

Do not install equipment until following conditions can be maintained in spaces to receive equipment:

Ambient temperature: 0 degrees to 40 degrees C (32 degrees to 104 degrees F).

Relative humidity: Maximum 90 percent, non-condensing.

Lighting control system must be protected from dust during installation.

WARRANTY

Provide Manufacturer’s Warranty:

Standard 2-year warranty, Includes:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First–Available Onsite or Remote Response Time

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Remote Diagnostics for Applicable Systems

Enhanced 8-year Silver Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Gold Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

72-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Platinum Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Coverage to Troubleshoot and Diagnose a Lighting Issue

24-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Provide Manufacturer’s Technology Support Plan for 8 years covering 100 percent parts and 100 percent Manufacturer labor and additional benefits as described below beginning 2 years after system startup completion.]

Silver Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Gold Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

72-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-year 100 Percent Manufacturer Warranty Labor Coverage to Gold Level Coverage.

Platinum Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage  to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days per Week Telephone Technical Support, excluding Manufacturer Holidays

24-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-Year 100 Percent Manufacturer Warranty Labor Coverage to Platinum Level Coverage.

MAINTENANCE Material Submittals

Make ordering of new equipment for expansions, replacements, and spare parts available to end user.

Make new replacement parts available for minimum of 10 years from date of manufacture.

- PRODUCTS

MANUFACTURERS

Basis of design product: Lutron Softswitch128 or subject to compliance and prior approval with specified requirements of this section, one of the following:

<Insert manufacturer’s name>

Substitutions: Under provisions of Division 1.

All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by the design professional a minimum of 10 working days prior to the bid date and must be made available to all bidders.   Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.  The contractor shall provide complete engineered shop drawings (including power wiring) with deviations for the original design highlighted in an alternate color to the engineer for review and approval prior to rough-in.

GENERAL

Provide hardware that is designed, tested, manufactured, and warranted by a single manufacturer.

Lighting Controls: Ten-year operational life while operating continually at any temperature in an ambient temperature range of 0 degrees C (32 degrees F) to 40 degrees C (104 degrees F) and 90 percent non-condensing relative humidity.

Designed and tested to withstand discharges without impairment of performance when subjected to discharges of 15,000 volts per IEC 801-2.

PANEL / RELAY PERFORMANCE REQUIREMENTS

Electrolytic capacitors to operate at least 20 degrees C below the component manufacturer's maximum temperature rating when device is under fully-loaded conditions in 40 degrees C (104 degrees F) ambient temperature.

Capable of withstanding repetitive inrush current of 50 times operating current without impacting lifetime of dimmer/relay.

Design and test relays to withstand line-side surges without impairment to performance.

Panels: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 3,000 amps per ANSI/IEEE C62.41B.

Utilize air gap off, activated when user selects “off” at any control to disconnect the load from line supply.

Possess power failure memory such that if power is interrupted and subsequently returned, lights will automatically return to same levels (on or off) prior to power interruption within 3 seconds.

Non-dim circuits to meet the following requirements:

Rated life of relay: Minimum 1,000,000 cycles.

Load switched in manner that prevents arcing at mechanical contacts when power is applied to load circuits.

Fully rated output continuous duty for inductive, capacitive, and resistive loads.

POWER PANELS

Product: Lutron Softswitch128

Mechanical:

Listed to UL 508 as industrial control equipment.

Delivered and installed as a UL listed factory assembled panel.

Field wiring accessible from front of panel without need to remove dimmer assemblies or other components.

Panels passively cooled via free-convection, unaided by fans or other means.

Ship panels with each relay in mechanical bypass position by means of jumper bar inserted between input and load terminals. Jumpers to carry full rated load current and be reusable at any time. Mechanical bypass device to allow for switching operation of connected load with relay removed by means of circuit breaker.

Flush into wall or Surface mounted.

Electrical:

Panels contain branch circuit protection for each circuit unless the panel is a dedicated feed-through type panel or otherwise indicated on the drawings.

Branch circuit breakers; meet following performance requirements:

Listed to UL 489 as molded case circuit breaker for use on lighting circuits.

Contain visual trip indicator; rated at 10,000 AIC.

Thermal-magnetic construction for overload, short-circuit, and over-temperature protection.  Use of breakers without thermal protection requires dimmers/relays to have integral thermal protection to prevent failures when overloaded or ambient temperature is above rating of panel.

Accept tag-out/lock-out devices to secure circuit breakers in off position when servicing loads.

Replaceable without moving or replacing dimmer/relay assemblies or other components in panel.

UL listed as switch duty (SWD) so that loads can be switched on and off by breakers.

Minimum UL listed Short Circuit Current Rating (SCCR) of 22,000A, 42,000A, 65,000A.

Rated life of relay: Minimum 1,000,000 cycles.

Load switched in manner that prevents arcing at mechanical contacts when power is applied to load circuits.

Fully rated output continuous duty for inductive, capacitive, and resistive loads.

LCD Panel Processor

System to be password protected.

Language selection: English

Integral contact closure inputs.

Programming and system operation:

Control stations, control interfaces, and contact closure inputs

Assign functionality of each control station button or infrared interface

Select patterns

Select customized pattern

Enable/Disable time clock

Initiate delay to off

Toggle one, some, or all zones

RS232 interface or Ethernet interface

Contact closure output: Momentary or maintained

Time clock

Integral astronomical time clock

Geographic location (city or latitude/longitude).

Adjustable date and time format.

Adjustable starting and ending of daylight savings time.

Review and modify time clock schedule to add, copy, modify, and delete events.

Overrides:

Set circuit status

Select pattern

Time clock override

Control station overrides

After-hours override

Diagnostics and Service:

Replacing relay does not require re-programming of system or processor.

Relays: Include diagnostic LED’s to verify proper operation and assist in system troubleshooting.

Relay panels: Include tiered control scheme for dealing with component failure that minimizes loss of control for occupant.

If lighting control system fails, lights to remain at current level. Panel processor provides local control of lights until system is repaired.

If panel processor fails, lights to remain at current level. Circuit breakers can be used to turn lights off or to full light output, allowing non-dim control of lights until panel processor is repaired.

If relay fails, factory-installed mechanical bypass jumpers to allow each relay to be mechanically bypassed. Mechanical bypass device to allow for switching operation of connected load with relay removed by means of circuit breaker.

LOW-VOLTAGE WALL STATIONS

Product: seeTouch or Key Switch.

Electronics:

Use RS485 wiring for low voltage communication.

Functionality:

Upon button press, LEDs to immediately illuminate.

LEDs to reflect the true system status.  LEDs to remain illuminated if the button press was properly processed or the LEDs turn off if the button press was not processed.

Allow for easy reprogramming without replacing unit.

Replacement of units does not require reprogramming.

Color:

Match NEMA WD1, Section 2.

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units.

Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Provide faceplates with concealed mounting hardware.

Engrave wall stations with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication.

Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

LOW VOLTAGE CONTROL INTERFACES

Contact Closure Interfaces; Lutron Model OMX-IO

The contact closure input device will accept both momentary and maintained contact closures.

The contact closure output device can be configured for maintained outputs.

Contact Closure Input Interfaces; Lutron Model OMX-WCI or Lutron seeTouch keypads SO-xx

The contact closure input device will accept both momentary and maintained contact closures.

Contact Closure Output Interface; Lutron Model OMX-CCO-8

The contact closure output device can be set for both momentary or maintained outputs.

Provide both normally open and normally closed contacts.

RS232 Interfaces; Lutron Model OMX-CI-RS232:

Provide ability to communicate by means of RS232 serial communication Softswitch 128 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 50 feet (15 meters) of RS232 source.

Provide access to:

Pattern selections.

Control individual zones.

Enable/disable time clock.

Setting of time clock.

Enable/disable wall station.

Simulate wall station button press.

Reading/setting of system variables.

Provide status monitoring through button feedback and pattern-status updates.

Ethernet Interfaces; Lutron Model OMX-CI-NWK-E:

Provide ability to communicate by means of TCP/IP over Ethernet to Softswitch128 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 300 feet (100 meters) of Ethernet source.

Provide access to:

Pattern selections.

Control individual zones.

Enable/disable time clock.

Setting of time clock.

Enable/disable wall station.

Simulate wall station button press.

Reading/setting of system variables.

Provide status monitoring through button feedback and pattern-status updates.

BACnet Interface; Lutron Model EM-A-BAC-xx-120:

Provide ability to communicate by means of BACnet IP or BACnet Ethernet communication to centralized lighting system from user-supplied 10BaseT Ethernet network.

Provide PIC list definition and object model to other system manufacturers.

LonWorks Interface; Lutron Model EM-A-LON-FT-120:

Provide ability to communicate by means of LonWorks FTT-10 communication to centralized lighting system from user-supplied LonWorks FTT-10 twisted pair network.

Provide LonWorks interface object model specification to secondary equipment manufacturers.

SENSORS

Ceiling and Wall Mount Occupancy/Vacancy Sensors

Product: LOS-CUS-500-WH, LOS-CUS-1000-WH, LOS-CUS-2000-WH, LOS-CIR-450-WH, LOS-CIR-1500-WH, LOS-CDT-500-WH, LOS-CDT-500R-WH, LOS-CDT-1000-WH, LOS-CDT-1000R-WH, LOS-CDT-2000-WH, LOS-CDT-2000R-WH, LOS-WIR-WH, LOS-WDT-WH, LOS-WDT-R-WH.

Sensing mechanism:

Infrared: Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Ultrasonic: Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Dual technology:

Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Connect directly to EcoSystem ballast and modules without the need of a power pack or other interface

Sensors shall turn off or reduce lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space

Sensor shall accommodate all conditions of space utilization and all irregular work hours and habits.

Sensors shall be UL listed

Sensors shall be fully adaptive and adjust their sensitivity and timing to ensure optimal lighting control for any use of the space

Sensors shall have field adjustable controls for time delay and sensitivity to override any adaptive features.

Power failure memory:

Controls incorporate non-volatile memory. Should power be interrupted and subsequently restored, settings and learned parameters saved in protected memory shall not be lost.

Provide all necessary mounting hardware and instructions.

Sensors shall be Class 2 devices.

Indicate viewing directions on mounting bracket for all Ceiling mount sensors.

Provide customizable mask to block off unwanted viewing areas for all ceiling mounted sensors using infrared technology.

Provide swivel mount base for all wall mount sensors.

Provide an internal additional isolated relay with Normally Open, Normally Closed and Common outputs for use with HVAC control, Data Logging and other control options.

Sensor Power Packs

For ease of mounting, installation and future service, power pack(s) shall be able to mount through a 1/2" knock-out in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power.  Transformer shall provide power to a minimum of three (3) sensors.

Power pack shall be plenum rated

Control wiring between sensors and control units shall be Class 2, 18-24 AWG, stranded U.L. Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable

Ceiling-Mounted Infrared Receivers Lutron Model OMX-CIR:

Shall have 360 degree reception of wireless infrared remote controls.

Exterior Daylight Sensors Lutron Model CES/O:

Calibrated with independent turn-on and turn-off thresholds; minimum 2 foot-candles difference between the turn-on and turn-off thresholds.

Enclosed in weatherproof housing with shading and lens protection visor.

ACCESSORIES

Tamper Proof Covers:

Locking covers for preset control units and wall stations: Reversible to allow lock to be located on either side of control.

Compatible with IR controls.

Does not reduce specified IR range by more than 50 percent of its original specification.

Infrared Transmitters:

Provide wireless remote control capable of recalling preset light levels for 4 or 8 patterns plus “off”.

Designed for use in conjunction with compatible infrared receiver and lighting control; dependent on that receiver, not transmitter.

Operate up to 50 feet (15 meters) within line-of-sight to that receiver.

“Learnable” by other variable frequency remote controls.

Emergency Lighting Interface; Lutron LUT-ELI

Provides total system listing to UL924 when used with Lutron Softswitch128 system.

Senses all three phases of building power.

Provides an output to power panels if power on any phase fails.

Accepts a contact closure input from a fire alarm control panel.

Expansion Module; Lutron Model XPS-E:

Provides:

3 low voltage control links

Master time clock

Master programmer

SOURCE QUALITY CONTROL

Perform full-function testing on completed assemblies at end of line. Statistical sampling is not acceptable.

- EXECUTION

INSTALLATION

Install equipment in accordance with manufacturer’s installation instructions.

Provide complete installation of system in accordance with Contract Documents.

Provide equipment at locations and in quantities indicated on Drawings. Provide any additional equipment required to provide control intent.

Mount daylight sensors to point due north with constant view of daylight.

Systems Integration:

Equipment Integration Meeting Visit (LSC-INT-VISIT)

Facility Representative to coordinate meeting between Facility Representative, Systems Integrator, Lighting Control System Manufacturer and other related equipment manufacturers to discuss equipment and integration procedures prior to system startup.

service and support

STARTUP AND PROGRAMMING

Provide telephone startup assistance to Electrical Contractor or End User Representative (when available, in accordance with manufacturer’s guidelines.  Otherwise, onsite startup will be utilized.)

        - Provides access to a Factory Certified Telephone Startup Technician during normal business hours.

        - Provides telephone instruction and guidance for a complete system functional test.

        - With phone startup completion and End User Registration, the 1-year parts-only warranty will be upgraded to the Standard 2-year Warranty.

Provide factory-certified field service engineer to make a site visit to ensure proper system installation and operation under following parameters:

Qualifications for factory-certified field service engineer:

Minimum experience of 2 years training in the electrical/electronic field.

Certified by the equipment manufacturer on the system installed.

Make a visit upon completion of installation of lighting control system:

Verify connection of power feeds and load circuits.

Verify connection and location of controls.

Verify proper connection of panel links (low voltage/data) and address panel.

Check load currents and remove by-pass jumpers.

Verify system operation control by control, circuit by circuit.

Verify proper operation of manufacturers interfacing equipment.

Obtain sign-off on system functions.

User to be trained on system operation.

Startup

After Hours Start-up (LSC-AH-SU)

Provide factory certified Field Service Engineer to perform manufacturer’s start-up procedures outside normal working hours (Monday through Friday, 7a.m. to 5 p.m.)

Tech Support

Provide factory direct technical support hotline 24 hours per day, 7 days per week.

FIELD QUALITY CONTROL

Manufacturer Services

Aim and Focus Visit (LSC-AF-VISIT)

Facility Representative to coordinate on-site meeting with Lighting Control System Manufacturer and Lighting Design Consultant to make required lighting adjustments to the system for conformance with the Lighting Design Consultant’s original design intent.]

System Optimization Visit (LSC-SYSOPT)

Lighting Control System Manufacturer to visit site 6 months after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.

CLOSEOUT ACTIVITIES

Training Visit (LSC-TRAINING)

Lighting Control System Manufacturer to provide 1 day additional on-site system training to site personnel.

On-site Walkthrough (LSC-WALK)

Lighting Control System Manufacturer to provide a factory certified Field Service Engineer to demonstrate system functionality to the Commissioning Agent.

MAINTENANCE

Capable of providing on-site service support within 24 hours anywhere in continental United States and within 72 hours worldwide except where special visas are required.

Offer renewable service contract on yearly basis, to include parts, factory labor, and annual training visits.  Make service contracts available up to ten years after date of system startup.

END OF SECTION