# SECTION 260933

# CENTRAL DIMMING CONTROLS

– GENERAL

SUMMARY

Section Includes:

Central dimming control systems.

Related Sections:

Section 262726 - Wiring Devices

Section 265113 – Interior Lighting Fixtures, Lamps, and Ballasts: Fluorescent electronic dimming ballasts.

Section 260923 – Lighting Control Devices: Occupancy sensors.

REFERENCES

American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE):

C62.41-1991 – Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

ASTM International (ASTM):

D4674 -02a Standard Test Method for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Fluorescent Lighting and Window-Filtered Daylight.

International Organization for Standardization (ISO):

9001:2000 – Quality Management Systems.

National Electrical Manufacturers Association (NEMA):

WD1 (R2005) - General Color Requirements for Wiring Devices.

Underwriters Laboratories, Inc. (UL):

489 (2002) - Molded-Case Circuit Breakers, Molded-Case Switches, and Circuit-Breaker Enclosures.

508 (1999) - Standard for Industrial Control Equipment.

1472 (1996) - Solid-State Dimming Controls.

924 (2003) - Emergency Lighting and Power Equipment

SYSTEM DESCRIPTION

Central dimming control system

Factory assembled dimming, switching panels, interfaces and modules.

Low voltage wall stations, control interfaces and sensors.

Solid-state high frequency fluorescent dimming ballasts.

SUBMITTALS

Submit under provisions of Section 013300.

Specification Conformance Document:  Indicate whether the submitted equipment either:

Meets specification exactly as stated.

Meets specification via an alternate means and indicate the specific methodology used.

Shop Drawings; include:

Load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, circuits that are on emergency, and capacity, phase, and corresponding circuit numbers.

Schematic of system.

Product Data: Catalog cut sheets with performance specifications demonstrating compliance with specified requirements.

CLOSEOUT SUBMITTALS

Sustainable Design Closeout Documentation (LSC-LEED-DOC)

Lighting Control System Manufacturer to provide Enhanced Startup documentation that details the start-up procedure being performed including a process to follow, details on tests performed and an area that documents any test results.

QUALITY ASSURANCE

Manufacturer: Minimum 10 years of experience in manufacture of architectural lighting controls.

Manufacturer’s Quality System: Registered to ISO 9001:2000 Quality Standards, including in-house engineering for product design activities.

Central dimming control system:

Listed by UL specifically for the required loads. Provide evidence of compliance upon request.

PROJECT CONDITIONS

Do not install equipment until following conditions can be maintained in spaces to receive equipment:

Ambient temperature: 0 degrees to 40 degrees C (32 degrees to 104 degrees F).

Relative humidity: Maximum 90 percent, non-condensing.

Lighting control system must be protected from dust during installation.

WARRANTY

Provide Manufacturer’s Warranty:

Standard 2-year warranty, Includes:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First–Available Onsite or Remote Response Time

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Remote Diagnostics for Applicable Systems

Enhanced 8-year Silver Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Gold Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

72-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Platinum Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Coverage to Troubleshoot and Diagnose a Lighting Issue

24-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Provide Manufacturer’s Technology Support Plan for 8] years covering 100 percent parts and 100 percent Manufacturer labor and additional benefits as described below beginning 2 years after system startup completion.

Silver Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Gold Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

72-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-year 100 Percent Manufacturer Warranty Labor Coverage to Gold Level Coverage.

Platinum Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days per Week Telephone Technical Support, excluding Manufacturer Holidays

24-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-Year 100 Percent Manufacturer Warranty Labor Coverage to Platinum Level Coverage.

For ballasts, see Section 265113 – Interior Lighting Fixtures, Lamps, and Ballasts.

MAINTENANCE

Make ordering of new equipment for expansions, replacements, and spare parts available to end user.

Make new replacement parts available for minimum of ten years from date of manufacture.

- PRODUCTS

MANUFACTURERS

Basis of design product: Lutron LCP128 or subject to compliance and prior approval with specified requirements of this section, one of the following:

<Insert manufacturer’s name>

Substitutions: Under provisions of Division 1.

All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by the design professional a minimum of 10 working days prior to the bid date and must be made available to all bidders.

Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.

Provide complete engineered shop drawings (including power wiring) with deviations for the original design highlighted in an alternate color to the engineer for review and approval prior to rough-in.

GENERAL

Provide hardware that is designed, tested, manufactured, and warranted by a single manufacturer.

Architectural Lighting Controls: Ten-year operational life while operating continually at any temperature in an ambient temperature range of 0 degrees C (32 degrees F) to 40 degrees C (104 degrees F) and 90 percent non-condensing relative humidity.

Designed and tested to withstand electrostatic discharges up to 15,000 V without impairment per IEC 801-2.

DIMMING / RELAY PERFORMANCE REQUIREMENTS

Electrolytic capacitors to operate at least 20 degrees C below the component manufacturer's maximum temperature rating when device is under fully-loaded conditions in 40 degrees C (104 degrees F) ambient temperature.

Load Handling Thyristors (SCRs and triacs), Field Effect Transistors (FETs), and Isolated Gate Bipolar Transistors (IGBTs): The component’s maximum current rating to be at least two times the dimmer’s/relay’s rated operating current.

Capable of withstanding repetitive inrush current of 50 times operating current without impacting lifetime of dimmer/relay.

Design and test dimmers/relays to withstand line-side surges without impairment to performance.

Panels: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 3,000 amps per ANSI/IEEE C62.41.

Utilize air gap off, activated when user selects “off” at any control to disconnect the load from line supply.

Power failure memory and dimmer/relay recovery:

When power is interrupted and subsequently returned, within 3 seconds lights will automatically return to same levels (dimmed setting, full on, or off) prior to power interruption.

Dimmers:

Provide real-time cycle-by-cycle compensation for incoming line voltage variations including changes in RMS voltage (plus or minus 2 percent change in RMS voltage/cycle), frequency shifts (plus or minus 2 Hz change in frequency/second), dynamic harmonics, and line noise.

Systems not providing cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

Each dimmer to incorporate electronic "soft-start" default at initial turn-on that smoothly ramps lights up to the appropriate levels within 0.5 seconds.

Control all light sources in smooth and continuous manor. Dimmers with visible steps are not acceptable.

Each dimmer to be assigned a load type that will provide a proper dimming curve for the specific light source.

Possess ability to have load types assigned per circuit, configured in field.

Minimum and maximum light levels user adjustable on output-by-output basis.

Line Voltage Dimmers; Meet following load-specific requirements:

Magnetic Low Voltage (MLV) transformer:

Contain circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472, Section 5.11.

Dimmers using unipolar load current devices (such as FETs or SCRs) to include DC current protection in the event of a single device failure.

Electronic Low Voltage (ELV) transformer:

Dimmer to operate electronic low voltage transformers via reverse phase control.  Alternately, forward phase control dimming may be used if dimming equipment manufacturer has recommended specific ELV transformers being provided.

Neon and cold cathode transformers:

Magnetic transformers: UL listed for use with normal (low) power factor magnetic transformers.

Electronic transformers: Must be supported by the ballast equipment manufacturer for control of specific ballasts being provided.

Fluorescent electronic dimming ballast: Refer to Section 265113 for dimming ballast specifications and performance.

Low Voltage Dimming Modules; Meet following requirements:

Coordination between low voltage dimming module and line voltage relay: Capable of being electronically linked to single zone.

Single low voltage dimming module; capable of controlling following light sources:

0-10V analog voltage signal.

Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

Sink current via IEC 60929.

Source current.

10-0V reverse analog voltage signal.

DSI digital communication.

DALI broadcast communication IEC 60929:

Logarithmic intensity values in compliance with IEC 60929.

Linear intensity values for use with LED color intensity control.

PWM IEC 60929.

Non-dim circuits to meet the following requirements:

Rated life of relay at full load: Minimum 1,000,000 cycles.

Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

Fully rated output continuous duty for inductive, capacitive, and resistive loads.

POWER PANELS

Product: LCP128 SpecGrade or LCP128 Standard Series.

Mechanical:

Listed to UL 508 as industrial control equipment.

Delivered and installed as a UL listed factory assembled panel.

Field wiring accessible from front of panel without need to remove dimmer assemblies or other components.

Panels passively cooled via free-convection, unaided by fans or other means.

Ship panels with each dimmer in mechanical bypass position by means of jumper bar inserted between input and load terminals. Jumpers to carry full rated load current and be reusable at any time. Mechanical bypass device to allow for switching operation of connected load with dimmer removed by means of circuit breaker.

Electrical:

Panels contain branch circuit protection for each input circuit unless the panel is a dedicated feed-through type panel or otherwise indicated on the drawings.

Branch circuit breakers; meet following performance requirements:

Listed to UL 489 as molded case circuit breaker for use on lighting circuits.

Contain visual trip indicator; rated at 10,000 AIC, 120 V Dimming, 14,000 AIC, 277 V Dimming, 18,000 AIC, 277 V Switching.

Thermal-magnetic construction for overload, short-circuit, and over-temperature protection.  Use of breakers without thermal protection requires dimmers/relays to have integral thermal protection to prevent failures when overloaded or ambient temperature is above rating of panel.

Accept tag-out/lock-out devices to secure circuit breakers in off position when servicing loads.

Replaceable without moving or replacing dimmer/relay assemblies or other components in panel.

UL listed as switch duty (SWD) so that loads can be switched on and off by breakers.

Minimum UL listed Short Circuit Current Rating (SCCR) of 25,000A, 45,000A or 65,000A.

Lutron LCP128 SpecGrade Series Grafik Panel; Architectural Lighting Control Panel:

Utilize universal 16A continuous-use UL listed dimmer.

Utilize multiple load type low voltage dimming module.

Limit current rise time to minimum 350 µsec as measured from 10-90 percent of load current waveform and minimum 525 µsec as measured from 0-100 percent of load current waveform at 50 percent rated dimmer capacity at a 90 degree conduction angle. Current rise to be minimum 400 µsec as measured from 10-90 percent of load current waveform and minimum 600 µsec as measured from 0-100 percent of load current waveform at 100 percent rated dimmer capacity at a 90 degree conduction angle.

Load faults only affect the given circuit.

Lutron LCP128 Panel; Light Duty Commercial Lighting Control Panel:

Flush into wall or Surface mounted

Utilize multiple load type 16A feed continuous-use UL listed dimming/switching modules.

For switching only circuits, utilize 1,000,000 cycle relay.

Utilize multiple load type low voltage dimming module.

LCD Panel Processor:

Separate password protection for installer and end user system settings.

Language selection: English

Integral contact closure inputs.

Programming and system operation:

Control stations, control interfaces, and contact closure devices:

Assign functionality of each control station button, infrared interface, key switch, or contact closure input:

Raise/lower one, some, or all lighting zones

Raise/stop/lower one, some, or all motorized zones

Toggle one, some, or all lighting zones

Select/Toggle scene

Raise/Lower scene

Enable/Disable time clock

Initiate delay to off

AV rack mounted interface: RS232 interface or Ethernet interface

Contact closure output: Momentary, maintained, or toggle.

DMX512 input: Maps DMX channel to a zone

Time clock

Integral astronomical time clock

Selectable geographic location (city or latitude/longitude).

Selectable time zone.

Selectable date and time format.

Adjustable starting and ending of daylight savings time.

Schedule adjustable to add, copy, modify, view, and delete events.

Assign functionality to time clock events:

Select global scene

Select customized scene

Enable/Disable all control stations (keypads)

Initiate delay to off

Enable/disable after hours mode

Emergency Mode

Automatic activation of predefined output intensities.

Disable control stations and time clock events.

Restore previous output intensities, enable control stations, and enable time clock events after deactivation of emergency mode.

After-hours Mode

User defined sequence is initiated by a time clock event to automatically turn specified outputs off:

5 minutes before switching off, system to flash dimmed/switched outputs 3 times to warn occupants.

Shut off sequence can be delayed by button press or occupancy sensor override for 30 minutes.

Repeat shut off sequence after the delay period.

Global Scene: Set and recall scene programming for multiple wall station locations.

Overrides:

Set output levels to On, Off, 0-100 percent, or Flash

Select global scenes

Enable/disable time clock

Enable/disable all control stations

Enable/disable after-hours

Diagnostics and Service:

Replacing dimmer/relay does not require re-programming of system or processor.

Dimmers/relays: Include diagnostic LED’s to verify proper operation and assist in system troubleshooting.

Dimming/relay panels: Include tiered control scheme for dealing with component failure that minimizes loss of control for occupant.

If lighting control system fails, lights to remain at current level. Panel processor provides local control of lights until system is repaired.

If panel processor fails, lights to remain at current level. Circuit breakers can be used to turn lights off or to full light output, allowing non-dim control of lights until panel processor is repaired.

If dimmer fails, factory-installed mechanical bypass jumpers to allow each dimmer to be mechanically bypassed. Mechanical bypass device to allow for switching operation of connected load with dimmer removed by means of circuit breaker.

POWER INTERFACES

Product: PHPM-PA-DV, PHPM-PA-120, PHPM-3F-DV, PHPM-3F-120, PHPM-SW-DV, GRX-TVI.

Electrical:

Phase independent of control input.

Dimmer to meet limited short circuit test as defined in UL 508.

Diagnostics and Service: Replacing power interface does not require re-programming of system or processor.

LOW-VOLTAGE WALL STATIONS

Product: seeTouch or Key Switch.

Electronics:

Use RS485 wiring for low voltage communication.

Functionality:

Upon button press, LEDs to immediately illuminate.

LEDs to reflect the true system status.  LEDs to remain illuminated if the button press was properly processed or the LEDs turn off if the button press was not processed.

Allow for easy reprogramming without replacing unit.

Replacement of units does not require reprogramming.

Color:

Match NEMA WD1, Section 2.

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units.

Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Provide faceplates with concealed mounting hardware.

Engrave wall stations in English with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication.

Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

LOW VOLTAGE CONTROL INTERFACES

Contact Closure Interfaces; Lutron Model OMX-IO

The contact closure input device will accept both momentary and maintained contact closures.

The contact closure output device can be configured for maintained or momentary outputs.

Contact Closure Input Interface; Lutron Model OMX-WCI or Lutron Model seeTouch keypads SO-xx

The contact closure input device will accept both momentary and maintained contact closures.

Contact Closure Output Interface; Lutron Model OMX-CCO-8

The contact closure output device can be configured for maintained or momentary outputs.

RS232; Lutron Model OMX-CI-RS232 or Ethernet Interfaces; Lutron Model OMX-CI-NWK-E:

Provide ability to communicate by means of user-supplied PC or digital audiovisual equipment.

Provide access to:

Scene selections.

Fade dimmed output to a level.

Ability to flash output levels.

Enable/disable time clock.

Enable/disable individual wall station.

Simulate wall station button press.

Fine tuning of light levels with individual output raise/lower.

Setting of time and date.

Provide status monitoring through button feedback and scene-status updates.

DXM-512 Interfaces; Lutron Model ODMX-512:

Control to be capable of mapping DMX-512 zones to LCP128 zones.

SENSORS

Ceiling-Mounted Infrared Receiver; Lutron Model OMX-CIR-WH:

Ceiling-Mounted Infrared Receivers have 360 degree reception of wireless infrared remote controls.

Exterior Daylight Sensors:

Calibrated with independent turn-on and turn-off thresholds; minimum 2 foot-candles difference between the turn-on and turn-off thresholds.

Enclosed in weatherproof housing with shading and lens protection visor.

Infrared Partition Sensor; Lutron Model GRX-IRPS-WH:

Provide contact closure based on status of sensor.

Ceiling and Wall Mount Occupancy/Vacancy Sensors

Product: LOS-CUS-500-WH, LOS-CUS-1000-WH, LOS-CUS-2000-WH, LOS-CIR-450-WH, LOS-CIR-1500-WH, LOS-CDT-500-WH, LOS-CDT-500R-WH, LOS-CDT-1000-WH, LOS-CDT-1000R-WH, LOS-CDT-2000-WH, LOS-CDT-2000R-WH, LOS-WIR-WH, LOS-WDT-WH, LOS-WDT-R-WH.

Sensing mechanism:

Infrared: Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Ultrasonic: Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Dual technology:

Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Sensors shall turn off or reduce lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space

Sensor shall accommodate all conditions of space utilization and all irregular work hours and habits.

Sensors shall be UL listed.

Sensors shall be fully adaptive and adjust their sensitivity and timing to ensure optimal lighting control for any use of the space.

Sensors shall have field adjustable controls for time delay and sensitivity to override any adaptive features.

Power failure memory:

Controls incorporate non-volatile memory. Should power be interrupted and subsequently restored, settings and learned parameters saved in protected memory shall not be lost.

Provide all necessary mounting hardware and instructions.

Sensors shall be Class 2 devices.

Indicate viewing directions on mounting bracket for all Ceiling mount sensors.

Provide customizable mask to block off unwanted viewing areas for all ceiling mounted sensors using infrared technology.

Provide swivel mount base for all wall mount sensors.

Provide an internal additional isolated relay with Normally Open, Normally Closed and Common outputs for use with HVAC control, Data Logging and other control options.

Sensor Power Packs

For ease of mounting, installation and future service, power pack(s) shall be able to mount through a 1/2" knock-out in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power.  Transformer shall provide power to a minimum of three (3) sensors.

Power pack shall be plenum rated

Control wiring between sensors and control units shall be Class 2, 18-24 AWG, stranded U.L. Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable

ACCESSORIES

Emergency Lighting Interface; Lutron LUT-ELI

Provides total system listing to UL924 when used with Lutron LCP128 system.

Senses all three phases of building power.

Provides an output to power panels if power on any phase fails.

Accepts a contact closure input from a fire alarm control panel.

Tamper Proof Covers:

Locking covers for preset control units and wall stations: Reversible to allow lock to be located on either side of control.

Compatible with IR controls.

Does not reduce specified IR range by more than 50 percent of its original specification.

Infrared Transmitters:

Provide wireless remote control.

Designed for use in conjunction with compatible infrared receiver and lighting control; compatibility dependent on that receiver, not transmitter.

Operate up to 15 meters (50 feet) within line-of-sight to that receiver.

“Learnable” by other variable frequency remote controls.

SOURCE QUALITY CONTROL

Perform full-function testing on 100 percent of all system components and panel assemblies at the factory.

- EXECUTION

INSTALLATION

Install equipment in accordance with manufacturer’s installation instructions.

Provide complete installation of system in accordance with Contract Documents.

Define each dimmer's/relay’s load type, assign each load to a zone, and set control functions.

Provide equipment at locations and in quantities indicated on drawings. Provide any additional equipment required to provide control intent.

Mount daylight sensors to point due north with constant view of daylight.

Systems Integration:

Equipment Integration Meeting Visit (LSC-INT-VISIT)

Facility Representative to coordinate meeting between Facility Representative, Lighting Control System Manufacturer and other related equipment manufacturers to discuss equipment and integration procedures.

SERVICE AND SUPPORT

Startup and Programming

Provide telephone startup assistance to Electrical Contractor or End User Representative (when available, in accordance with manufacturer’s guidelines.  Otherwise, onsite startup will be utilized.)

        - Provides access to a Factory Certified Telephone Startup Technician during normal business hours.

        - Provides telephone instruction and guidance for a complete system functional test.

        - With phone startup completion and End User Registration, the 1-year parts-only warranty will be upgraded to the Standard 2-year Warranty.

Provide factory-certified field service engineer to a site visit to ensure proper system installation and operation under following parameters:

Qualifications for factory-certified field service engineer:

Minimum experience of 2 years training in the electrical/electronic field.

Certified by the equipment manufacturer on the system installed.

Make a visit upon completion of installation of central dimming control system:

Verify connection of power feeds and load circuits.

Verify connection and location of controls.

Verify proper connection of panel links (low voltage/data) and address panel.

Check dimming/switching panel load types and currents and remove by-pass jumpers.

Verify system operation control by control, circuit by circuit.

Verify proper operation of supplied interfacing equipment to other devices.

Obtain sign-off on system functions.

User to be trained on system operation.

After Hours Start-up (LSC-AH-SU)

Provide factory certified Field Service Engineer to perform manufacturer’s start-up procedures outside normal working hours (Monday through Friday, 7a.m. to 5 p.m.)

Tech Support

Provide factory direct technical support hotline 24 hours per day, 7 days per week.

FIELD QUALITY CONTROL

Manufacturer Services

Aim and Focus Visit (LSC-AF-VISIT)

Facility Representative to coordinate on-site meeting with Lighting Control System Manufacturer and Lighting Design Consultant to make required lighting adjustments to the system for conformance with the Lighting Design Consultant’s original design intent.]

System Optimization Visit (LSC-SYSOPT)

Lighting Control System Manufacturer to visit site 6 months after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.

CLOSEOUT ACTIVITIES

Training Visit (LSC-TRAINING)

Lighting Control System Manufacturer to provide 1 day additional on-site system training to site personnel.

On-site Walkthrough (LSC-WALK)

Lighting Control System Manufacturer to provide a factory certified Field Service Engineer to demonstrate system functionality to the Commissioning Agent.

MAINTENANCE

Capable of providing on-site service support within 24 hours anywhere in continental United States and within 72 hours worldwide except where special visas are required.

Offer renewable service contract on yearly basis, to include parts, factory labor, and annual training visits.  Make service contracts available up to ten years after date of system startup.

END OF SECTION