# SECTION 260936

# MODULAR DIMMING CONTROLS

- GENERAL

SUMMARY

Section Includes:

Modular dimming control systems.

Related Sections:

Section 122000 - Window Treatments: Window treatments controlled by modular dimming control system.

Section 262726 - Wiring Devices

Section 265113 – Interior Lighting Fixtures, Lamps, and Ballasts: Fluorescent lighting ballasts controlled by modular dimming control system.

Section 260923 – Lighting Control Devices: Occupancy sensors used in conjunction with modular dimming control system.

REFERENCES

American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE)

C62.41-1991 – Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

ASTM International (ASTM)

D4674 -02a Standard Test Method for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Fluorescent Lighting and Window-Filtered Daylight.

International Organization for Standardization (ISO)

9001:2000 – Quality Management Systems.

National Electrical Manufacturers Association (NEMA)

WD1 (R2005) - General Color Requirements for Wiring Devices.

Underwriters Laboratories, Inc. (UL)

508 (1999) - Standard for Industrial Control Equipment.

1472 (1996) - Solid-State Dimming Controls.

924 (2003) - Emergency Lighting and Power Equipment

SYSTEM DESCRIPTION

Modular dimming control system

Factory assembled dimming controls, interfaces and modules.

Low voltage wall stations, control interfaces and sensor.

Solid-state high frequency fluorescent dimming ballasts.

SUBMITTALS

Submit under provisions of Section 013300.

Specification Conformance Document:  Indicate whether the submitted equipment:

Meets specification exactly as stated.

Meets specification via an alternate means and indicate the specific methodology used.

Shop Drawings; include:

Load schedule indicating actual connected load, load type, and voltage per circuit, circuits and their respective control zones, circuits that are on emergency, and capacity, phase, and corresponding circuit numbers.

Schematic of system.

Product Data: Catalog cut sheets with performance specifications demonstrating compliance with specified requirements.

CLOSEOUT SUBMITTALS

Sustainable Design Closeout Documentation (LSC-LEED-DOC)

Lighting Control System Manufacturer to provide LEED commissioning documentation that details the start-up procedure being performed including a process to follow, details on tests performed and an area that documents any test results.

QUALITY ASSURANCE

Manufacturer: Minimum 10 years of experience in manufacture of architectural lighting controls.

Manufacturer’s Quality System: Registered to ISO 9001:2000 Quality Standards, including in-house engineering for product design activities.

Modular dimming control system:

Listed by UL specifically for the required loads. Provide evidence of compliance upon request.

PROJECT CONDITIONS

Do not install equipment until following conditions can be maintained in spaces to receive equipment:

Ambient temperature: 0 degrees to 40 degrees C (32 degrees to 104 degrees F).

Relative humidity: Maximum 90 percent, non-condensing.

Lighting control system must be protected from dust during installation.

WARRANTY

Provide Manufacturer’s Warranty:

Standard 2-year warranty, Includes:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First–Available Onsite or Remote Response Time

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Remote Diagnostics for Applicable Systems

Enhanced 8-year Silver Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Gold Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

72-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Enhanced 8-year Platinum Level limited parts warranty, Includes:

Years 1-2:

100 Percent Replacement Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Coverage to Troubleshoot and Diagnose a Lighting Issue

24-Hour Onsite or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Years 3-5:  50% Replacement Parts Coverage

Years 6-8:  25% Replacement Parts Coverage

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

Provide Manufacturer’s Technology Support Plan for 8 years covering 100 percent parts and 100 percent Manufacturer labor and additional benefits as described below beginning 2 years after system startup completion.

Silver Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

First-Available Onsite or Remote Response Time

Remote Diagnostics for Applicable Systems

Gold Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days Per Week Telephone Technical Support, Excluding Manufacturer Holidays

72-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-year 100 Percent Manufacturer Warranty Labor Coverage to Gold Level Coverage.

Platinum Level Technology Support Plan, Includes:

100 Percent Parts for Manufacturer Lighting System Components

100 Percent Manufacturer Labor Coverage  to Troubleshoot and Diagnose a Lighting Issue

24 Hours Per Day, 7 Days per Week Telephone Technical Support, excluding Manufacturer Holidays

24-Hour On-Site or Remote Response Time

Annual Scheduled Preventive Maintenance Visit

Remote Diagnostics for Applicable Systems

Includes Service Coverage Upgrade of the Initial 2-Year 100 Percent Manufacturer Warranty Labor Coverage to Platinum Level Coverage.

For ballasts, see Section 265113 – Interior Lighting Fixtures, Lamps, and Ballasts.

For Sivoia QED shades, see section 122413 – Roller Window Shades: Sivoia QED.

MAINTENANCE

Make ordering of new equipment for expansions, replacements, and spare parts available to end user.

Make new replacement parts available for minimum of ten years from date of manufacture.

- PRODUCTS

MANUFACTURERS

Basis of design product: Lutron GRAFIK Eye 3000 or subject to compliance and prior approval with specified requirements of this section, one of the following:

<Insert manufacturer’s name>

Substitutions: Under provisions of Division 1.

All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by the design professional a minimum of 10 working days prior to the bid date and must be made available to all bidders.

Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.

Provide complete engineered shop drawings (including power wiring) with deviations for the original design highlighted in an alternate color to the engineer for review and approval prior to rough-in.

GENERAL

Provide system hardware that is designed, tested, manufactured, and warranted by a single manufacturer.

Architectural Lighting Controls: Ten-year operational life while operating continually at any temperature in an ambient temperature range of 0 degrees C (32 degrees F) to 40 degrees C (104 degrees F) and 90 percent non-condensing relative humidity.

Designed and tested to withstand electrostatic discharges up to 15,000 V without impairment per IEC 801-2.

DIMMING PERFORMANCE REQUIREMENTS

Electrolytic capacitors to operate at least 20 degrees C below the component manufacturer's maximum temperature rating when device is under fully-loaded conditions in 40 degrees C (104 degrees F) ambient temperature.

Load Handling Thyristors (SCRs and triacs), Field Effect Transistors (FETs), and Isolated Gate Bipolar Transistors (IGBTs): Manufacturer’s maximum current rating minimum two times control’s rated operating current.

Capable of withstanding repetitive inrush current of 50 times operating current without impacting lifetime of dimmer.

Design and test dimmers to withstand line-side surges without impairment to performance.

Control Units: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 3,000 amps per ANSI/IEEE C62.41 and per IEC 61000-4-5 surge requirements.

Other power handling devices: Withstand surges without impairment of performance when subjected to surges of 6,000 volts, 200 amps per ANSI/IEEE C62.41.

Utilize air gap off, activated when user selects “off” at any control to disconnect the load from line supply.

Possess power failure memory such that if power is interrupted and subsequently returned, lights will automatically return to same levels (dimmed setting, full on, or off) prior to power interruption within 3 seconds.

Multiple load type, tested to UL 508 to specifically control incandescent/tungsten, magnetic low voltage, electronic low voltage, neon/cold cathode, fluorescent dimming ballasts, and non-dim loads.

Each dimmer to be assigned a load type that will provide a proper dimming curve for the specific light source.

Possess ability to have load types assigned per circuit, configured in field.

Minimum and maximum light levels user adjustable on circuit-by-circuit basis.

Control all light sources in smooth and continuous manor. Dimmers with visible steps are not acceptable.

Provide real-time cycle-by-cycle compensation for incoming line voltage variations including changes in RMS voltage (plus or minus 2 percent change in RMS voltage/cycle), frequency shifts (plus or minus 2 Hz change in frequency/second), dynamic harmonics, and line noise. Systems not providing cycle-by-cycle compensation to include external power conditioning equipment to meet these requirements.

Systems not providing cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

Each dimmer to incorporate electronic "soft-start" default at initial turn-on that smoothly ramps lights up to the appropriate levels within 0.5 seconds.

Line Voltage Dimmers; Meet following load-specific requirements:

Magnetic Low Voltage (MLV) transformer:

Contain circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472, Section 5.11.

Dimmers using back-to-back SCR construction that could fail open causing DC power to flow into magnetic low voltage load are not acceptable.

Electronic Low Voltage (ELV) transformer:

Dimmer to operate electronic low voltage transformers via reverse phase control.  Alternately, forward phase control dimming may be used if dimming equipment manufacturer has recommended specific ELV transformers being provided.

Neon and cold cathode transformers:

Magnetic transformers: UL listed for use with normal (low) power factor magnetic transformers.

Electronic transformers: Must be supported by the ballast equipment manufacturer for control of specific ballasts being provided.

Fluorescent electronic dimming ballast: Refer to Section 265113 for dimming ballast specifications and performance.

Low Voltage Dimming Interface; Meet following requirements:

Coordination between low voltage dimming module and line voltage relay: Capable of being electronically linked to single zone.

Single low voltage dimming module; capable of controlling following light sources:

0-10V analog voltage signal.

Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

Sink current via IEC 60929.

POWER INTERFACES

Product: PHPM-PA-DV, PHPM-PA-120, PHPM-3F-DV, PHPM-3F-120, PHPM-SW-DV or GRX-TVI.

Electrical:

Phase independent of control input.

Dimmer to meet limited short circuit test as defined in UL 20.

Diagnostics and Service: Replacing power interface does not require re-programming of system or processor.

WALL STATIONS

Line Voltage Wall Stations:

Preset Lighting Control with Zone Override; Lutron Grafik Eye GRX-3100 or Lutron Grafik Eye GRX-3500:

Intensity for each zone indicated by means of one illuminated bar graph per zone.

Fade time indicated by digital display for current scene while fading.

Incorporate built-in wide angle infrared receiver.

For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

Low Voltage Wall Stations:

Product: seeTouch or Key Switch.

Electronics:

Use RS485 wiring for low voltage communication.

Functionality:

Upon button press, LEDs to immediately illuminate.

LEDs to reflect the true system status.  LEDs to remain illuminated if the button press was properly processed or the LEDs turn off if the button press was not processed.

Allow for easy reprogramming without replacing unit.

Replacement of units does not require reprogramming.

Provide faceplates with concealed mounting hardware.

Engrave wall stations with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication.

Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

Color:

Match NEMA WD1, Section 2.

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units.

Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Provide faceplates with concealed mounting hardware.

Engrave wall stations with appropriate button, zone, and scene engraving descriptions furnished prior to fabrication.

Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

LOW VOLTAGE CONTROL INTERFACES

Contact Closure Interfaces; Lutron Model GRX-IO

The contact closure input device will accept both momentary and maintained contact closures.

The contact closure output device can be configured for maintained or momentary outputs.

Contact Closure Input Interface; Lutron Model GRX-WCI or Lutron Model seeTouch keypads SG-xx

The contact closure input device will accept both momentary and maintained contact closures.

Contact Closure Output Interface; Lutron Model GRX-CCO-8

The contact closure output device can be configured for maintained or momentary outputs.

Astronomical Timeclock and Programmer Interface; Lutron Model GRX-CI-PRG:

Provide ability to communicate by means of RS232 serial communication to GRX-4000 series system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 50 feet (15 meters) of RS232 source.

Provide ability to communicate by means of TCP/IP over Ethernet to GRAFIK Eye 4000 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 300 feet (100 meters) of Ethernet source.

Astronomical time clock and programmer interface

Provide access to:

Scene selections.

Fade zone to a level.

Fine-tuning of preset levels with scene raise/lower.

Lock out scenes and zones.

Fine-tuning of light levels with individual zone raise/lower.

Enable/disable wall station.

Software to provide as follows:

System setup

Program low voltage controls.

Set up and run time clock schedules.

Set up and run sequences.

Set and report time.

Archive system information.

Provide status monitoring through button feedback and scene-status updates.

Ethernet Interfaces; Lutron Model GRX-CI-NWK-E: RS232 Interface; Lutron Model GRX-CI-RS232:

RS232 Interface

Provide ability to communicate by means of RS232 serial communication to GRX-4000 series system by means of user-supplied PC or digital audiovisual equipment. Control to be located within 15 meters (50 feet) of RS232 source.

Ethernet Interface

Provide ability to communicate by means of TCP/IP over Ethernet to GRAFIK Eye 4000 system by means of user-supplied PC or digital audiovisual equipment. Control to be located within (1000 meters (300 feet) of Ethernet source.

RS232 and Ethernet Interface

Provide access to:

Scene selections.

Fade zone to a level.

Fine-tuning of preset levels with scene raise/lower.

Lock out scenes and zones.

Fine-tuning of light levels with individual zone raise/lower.

Enable/disable wall station.

Provide status monitoring through button feedback and scene-status updates.

Infrared Interface; Lutron GRX-IRI:

Integrate third party infrared controls into preset lighting control system.

Sivoia Quiet Electronic Drive (QED) Controller; Lutron Model SG-SVCN:

Integrate control of QED shades into preset lighting control system.

AC Motor Group Controller; Lutron Model GRX-4M-GC:

Integrate control of AC motor shades into preset lighting control system.

Radio Frequency Interface; Lutron Model RA-GRXI-WH:

GRAFIK Eye preset lighting control to be controlled by radio frequency.

Automatic Daylighting Control Interface; Lutron Model GRX-DACPI:

Provide automatic scene selection in response to ambient daylight

SENSORS

Ceiling-Mounted Infrared Receiver; Lutron Model GRX-CIR-WH:

Ceiling-Mounted Infrared Receivers have 360 degree reception of wireless infrared remote controls.

Interior Daylight Sensors; Lutron Model MW-FPS-WH:

Use Class 2 wiring for low voltage communication

Can be replaced without reprogramming

Open-loop basis for daylight sensor control scheme

Stable output over temperature from 0 degrees C to 40 degrees C

Partially shielded for accurate detection of available daylight to prevent fixture lighting and horizontal light component from skewing sensor detection

Provide linear response from 0 to 500 foot-candles

Constructed with plastic meeting UL94 HB

Mountable on lighting fixtures or recessed acoustical ceiling tiles

Constructed via sonic welding

Color:

Match NEMA WD1, Section 2 White

Color variation in same product family: Maximum ΔE=1, CIE L*a*b color units

Visible parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

Exterior Daylight Sensors:

Calibrated with independent turn-on and turn-off thresholds; minimum 2 foot-candles difference between the turn-on and turn-off thresholds.

Enclosed in weatherproof housing with shading and lens protection visor.

Infrared Partition Sensor; Lutron Model GRX-IRPS-WH:

Provide contact closure based on status of sensor.

Ceiling and Wall Mount Occupancy/Vacancy Sensors

Product: LOS-CUS-500-WH, LOS-CUS-1000-WH, LOS-CUS-2000-WH, LOS-CIR-450-WH, LOS-CIR-1500-WH, LOS-CDT-500-WH, LOS-CDT-500R-WH, LOS-CDT-1000-WH, LOS-CDT-1000R-WH, LOS-CDT-2000-WH, LOS-CDT-2000R-WH, LOS-WIR-WH, LOS-WDT-WH, LOS-WDT-R-WH.

Sensing mechanism:

Infrared: Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Ultrasonic: Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Dual technology:

Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

Utilize an operating frequency of 32kHz or 40kHz that shall be crystal controlled to operate within plus or minus 0.005 percent tolerance.

Sensors shall turn off or reduce lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space

Sensor shall accommodate all conditions of space utilization and all irregular work hours and habits.

Sensors shall be UL listed (as appropriate)

Sensors shall be fully adaptive and adjust their sensitivity and timing to ensure optimal lighting control for any use of the space

Sensors shall have field adjustable controls for time delay and sensitivity to override any adaptive features.

Power failure memory:

Controls incorporate non-volatile memory. Should power be interrupted and subsequently restored, settings and learned parameters saved in protected memory shall not be lost.

Provide all necessary mounting hardware and instructions.

Sensors shall be Class 2 devices.

Indicate viewing directions on mounting bracket for all Ceiling mount sensors.

Provide customizable mask to block off unwanted viewing areas for all ceiling mounted sensors using infrared technology.

Provide swivel mount base for all wall mount sensors.

Provide an internal additional isolated relay with Normally Open, Normally Closed and Common outputs for use with HVAC control, Data Logging and other control options.

Sensor Power Packs

For ease of mounting, installation and future service, power pack(s) shall be able to mount through a 1/2" knock-out in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power.  Transformer shall provide power to a minimum of three (3) sensors.

Power pack shall be plenum rated

Control wiring between sensors and control units shall be Class 2, 18-24 AWG, stranded U.L. Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable

ACCESSORIES

Emergency Lighting Interface; Lutron LUT-ELI

Provides total system listing to UL924 when used with Lutron GRAFIK Eye 4000 system.

Senses all three phases of building power.

Provides an output to power panels if power on any phase fails.

Accepts a contact closure input from a fire alarm control panel.

Tamper Proof Covers:

Locking covers for preset control units and wall stations: Reversible to allow lock to be located on either side of control.

Compatible with IR controls.

Does not reduce specified IR range by more than 50 percent of its original specification.

Infrared Transmitters:

Provide wireless remote control capable of recalling preset light levels for [four] [eight] scenes plus “off” and of fine-tuning light levels with master raise/lower.

Designed for use in conjunction with compatible infrared receiver and lighting control; dependent on that receiver, not transmitter.

Operate up to 15 meters (50 feet) within line-of-sight to that receiver.

“Learnable” by other variable frequency remote controls.

SOURCE QUALITY CONTROL

Perform full-function testing on completed assemblies at end of line. Statistical sampling is not acceptable.

- EXECUTION

INSTALLATION

Install equipment in accordance with manufacturer’s installation instructions.

Provide complete installation of system in accordance with Contract Documents.

Define each dimmer's load type, assign each load to a zone, and set control functions.

Provide equipment at locations and in quantities indicated on Drawings. Provide any additional equipment required to provide control intent.

Mount daylight sensors to point due north with constant view of daylight.

Ensure that daylight sensor placement minimizes sensors view of electric light sources; ceiling mounted and fixture-mounted daylight sensors shall not have direct view of luminaries.

Systems Integration:

Equipment Integration Meeting Visit (LSC-INT-VISIT)

Facility Representative to coordinate meeting between Facility Representative, Lighting Control System Manufacturer and other related equipment manufacturers to discuss equipment and integration procedures.

SERVICE AND SUPPORT

Startup and Programming

Provide telephone startup assistance to Electrical Contractor or End User Representative (when available, in accordance with manufacturer’s guidelines.  Otherwise, onsite startup will be utilized.)

        - Provides access to a Factory Certified Telephone Startup Technician during normal business hours.

        - Provides telephone instruction and guidance for a complete system functional test.

        - With phone startup completion and End User Registration, the 1-year parts-only warranty will be upgraded to the Standard 2-year Warranty.]

Provide factory-certified field service engineer to a site visit to ensure proper system installation and operation under following parameters:

Qualifications for factory-certified field service engineer:

Minimum experience of 2 years training in the electrical/electronic field.

Certified by the equipment manufacturer on the system installed.

Make a visit upon completion of installation of modular dimming control system:

Verify connection of power feeds and load circuits.

Verify connection and location of controls.

Program system data.

Verify proper connection of digital control link.

Verify proper operation of manufacturers interfacing equipment.

Obtain sign-off on system functions.

User to be trained on system operation.

After Hours Start-up (LSC-AH-SU)

Provide factory certified Field Service Engineer to perform manufacturer’s start-up procedures outside normal working hours (Monday through Friday, 7a.m. to 5 p.m.)]

Tech Support

Provide factory direct technical support hotline 24 hours per day, 7 days per week.

FIELD QUALITY CONTROL

Manufacturer Services

Aim and Focus Visit (LSC-AF-VISIT)

Facility Representative to coordinate on-site meeting with Lighting Control System Manufacturer and Lighting Design Consultant to make required lighting adjustments to the system for conformance with the Lighting Design Consultant’s original design intent.]

System Optimization Visit (LSC-SYSOPT)

Lighting Control System Manufacturer to visit site 6 months after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.]

CLOSEOUT ACTIVITIES

Training Visit (LSC-TRAINING)

Lighting Control System Manufacturer to provide 1 day additional on-site system training to site personnel.

On-site Walkthrough (LSC-WALK)

Lighting Control System Manufacturer to provide a factory certified Field Service Engineer to demonstrate system functionality to the Commissioning Agent.

MAINTENANCE

Capable of providing on-site service support within 24 hours anywhere in continental United States and within 72 hours worldwide except where special visas are required.

Offer renewable service contract on yearly basis, to include parts, factory labor, and annual training visits.  Make service contracts available up to ten years after date of system startup.

END OF SECTION