SECTION 26 0943

NETWORK LIGHTING CONTROLS

- GENERAL

  - SECTION INCLUDES

    - Digital-network lighting control system and associated components:

      - Power panels.

      - Fluorescent electronic dimming ballasts.

      - LED drivers.

      - Power interfaces.

      - Main units.

      - Lighting control modules.

      - Energy meter.

      - Digital dimming ballast and switching modules.

      - Lighting management hubs.

      - Lighting management system computers.

      - Lighting management system software.

      - Control stations.

      - Low-voltage control interfaces.

      - Wired sensors.

      - Wireless sensors.

      - Accessories.

  - RELATED REQUIREMENTS

    - Section 12 2400 - Window Shades: Motorized roller window shades, for interface with lighting control system.

    - Section 25 5600 - Building automation system, for interface with lighting control system.

    - Section 26 0553 - Identification for Electrical Systems:  Identification products and requirements.

    - Section 26 2726 - Wiring Devices:

      - Finish requirements for wall controls specified in this section.

      - Accessory receptacles and wallplates, to match lighting controls specified in this section.

    - Section 26 5113 - Luminaires, Ballasts, and Drivers

    - Section 27 4113 - Audio-video system, for interface with lighting control system.

  - REFERENCE STANDARDS

    - ANSI C12.20 - American National Standard for Electricity Meters - 0.2 and 0.5 Accuracy Classes.

    - ANSI C82.11 - American National Standard for Lamp Ballasts - High Frequency Fluorescent Lamp Ballasts - Supplements.

    - ANSI/ESD S20.20 - Protection of Electrical and Electronic Parts, Assemblies and Equipment (Excluding Electrically Initiated Explosive Devices).

    - ASTM D4674 - Standard Practice for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Office Environments.

    - IEC 60669-2-1 - Switches for Household and Similar Fixed Electrical Installations - Part 2-1: Particular Requirements - Electronic Switches.

    - IEC 60929 - AC and/or DC-Supplied Electronic Control Gear for Tubular Fluorescent Lamps - Performance Requirements.

    - IEC 61000-4-2 - Electromagnetic Compatibility (EMC) - Part 4-2: Testing and Measurement Techniques - Electrostatic Discharge Immunity Test.

    - IEC 61000-4-5 - Electromagnetic Compatibility (EMC) - Part 4-5: Testing and Measurement Techniques - Surge Immunity Test.

    - IEC 61347-2-3 - Lamp Control Gear - Part 2-3: Particular Requirements for A.C. and/or D.C. Supplied Electronic Control Gear for Fluorescent Lamps.

    - IEC 61347-2-13 - Lamp Control Gear - Part 2-13: Particular Requirements for D.C. or A.C. Supplied Electronic Control Gear for LED Modules.

    - IEEE C62.41.2 - Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and less) AC Power Circuits.

    - ISO 9001 - Quality Management Systems-Requirements.

    - NECA 1 - Standard for Good Workmanship in Electrical Construction.

    - NECA 130 - Standard for Installing and Maintaining Wiring Devices; National Electrical Contractors Association.

    - NEMA 410 - Performance Testing for Lighting Controls and Switching Devices with Electronic Drivers and Discharge Ballasts; National Electrical Manufacturers Association.

    - NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers Association.

    - NFPA 70 - National Electrical Code; National Fire Protection Association.

    - UL 94 - Tests for Flammability of Plastic Materials for Parts in Devices and Appliances.

    - UL 489 - Molded-Case Circuit Breakers, Molded-Case Switches and Circuit Breaker Enclosures.

    - UL 508 - Industrial Control Equipment; Underwriters Laboratories Inc.

    - UL 508A - Industrial Control Panels; Underwriters Laboratories Inc.

    - UL 924 - Emergency Lighting and Power Equipment.

    - UL 935 - Fluorescent-Lamp Ballasts.

    - UL 1472 - Solid-State Dimming Controls.

    - UL 2043 - Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

    - UL 8750 - Light Emitting Diode (LED) Equipment for Use in Lighting Products.

  - ADMINISTRATIVE REQUIREMENTS

    - Coordination:

      - Coordinate the placement of sensors and wall controls with millwork, furniture, equipment, etc. installed under other sections or by others.

      - Coordinate the placement of wall controls with actual installed door swings.

      - Coordinate the placement of daylight sensors with windows, skylights, and luminaires to achieve optimum operation. Coordinate placement with ductwork, piping, equipment, or other potential obstructions to light level measurement installed under other sections or by others.

      - Where motorized window treatments are to be controlled by the lighting control system provided under this section, coordinate the work with other trades to provide compatible products.

      - Coordinate the work to provide luminaires and lamps compatible with the lighting controls to be installed.

      - Notify Architect of any conflicts or deviations from the contract documents to obtain direction prior to proceeding with work.

    - Preinstallation Meeting: Conduct on-site meeting with lighting control system manufacturer prior to commencing work as part of manufacturer's standard startup services. Manufacturer to review with installer:

      - Low voltage wiring requirements.

      - Separation of power and low voltage/data wiring.

      - Wire labeling.

      - Lighting management hub locations and installation.

      - Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS", sensor locations to be reviewed in accordance with layout provided by Lighting Control Manufacturer. Lighting Control Manufacturer may direct Contractor regarding sensor relocation should conditions require a deviation from locations indicated.

      - Control locations.

      - Computer jack locations.

      - Load circuit wiring.

      - Network wiring requirements.

      - Connections to other equipment.

      - Installer responsibilities.

      - Power panel locations.

    - Sequencing:

      - Do not install sensors and wall controls until final surface finishes are complete.

  - SUBMITTALS

    - See Section 01 3000 - Administrative Requirements for submittal procedures.

    - Design Documents: Where Lighting Control Manufacturer Sensor Layout and Tuning service is specified in Part 2 under "DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS", Lighting Control Manufacturer to provide plans indicating occupancy/vacancy and/or daylight sensor locations.

    - Product Data: Include ratings, configurations, standard wiring diagrams, dimensions, colors, service condition requirements, and installed features.

      - Occupancy/Vacancy Sensors: Include detailed basic motion detection coverage range diagrams.

    - Shop Drawings:

      - Provide schematic system riser diagram indicating component interconnections. Include requirements for interface with other systems.

      - Provide detailed sequence of operations describing system functions.

    - Manufacturer's Installation Instructions: Include application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, and installation of product.

    - Project Record Documents: Record actual installed locations and settings for lighting control system components.

    - System Performance-Verification Documentation; LSC-SPV-DOC: Include additional costs for manufacturer's enhanced documentation detailing start-up performance-verification procedures and functional tests performed along with test results.

    - Operation and Maintenance Data: Include detailed information on lighting control system operation, equipment programming and setup, replacement parts, and recommended maintenance procedures and intervals.

    - Warranty: Submit sample of manufacturer's Warranty or Enhanced Warranty as specified in Part 1 under "WARRANTY". Submit documentation of final execution completed in Owner's name and registered with manufacturer.

    - Software: One copy of software provided under this section.

  - QUALITY ASSURANCE

    - Conform to requirements of NFPA 70.

    - Maintain at the project site a copy of each referenced document that prescribes execution requirements.

    - Manufacturer Qualifications:

      - Company with not less than ten years of experience manufacturing lighting control systems of similar complexity to specified system.

      - Registered to ISO 9001, including in-house engineering for product design activities.

      - Qualified to supply specified products and to honor claims against product presented in accordance with warranty.

    - Maintenance Contractor Qualifications: Manufacturer's authorized service representative.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in a clean, dry space in original manufacturer's packaging in accordance with manufacturer's written instructions until ready for installation.

  - FIELD CONDITIONS

    - Maintain field conditions within manufacturer's required service conditions during and after installation.

      - System Requirements, Unless Otherwise Indicated:

        - Ambient Temperature:

          - Lighting Control System Components, Except Those Listed Below: Between 32 and 104 degrees F (0 and 40 degrees C).

          - Lighting Management System Computer: Between 50 and 90 degrees F (10 and 35 degrees C).

          - Fluorescent Electronic Dimming Ballasts: Between 50 and 140 degrees F (10 and 60 degrees C).

        - Relative Humidity: Less than 90 percent, non-condensing.

  - WARRANTY

    - See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

    - Manufacturer's Standard Warranty with manufacturer Start-Up; 2-Year Warranty:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - 100 percent replacement parts coverage, 100 percent manufacturer labor coverage to troubleshoot and diagnose a lighting issue.

          - First-available on-site or remote response time.

          - Remote diagnostics for applicable systems.

        - Telephone Technical Support: Available 24 hours per day, 7 days per week, excluding manufacturer holidays.

      - Lighting Management System Computer: One year 100 percent parts coverage, one year 100 percent manufacturer labor coverage.

      - Ballasts/Drivers and Ballast Modules: Five years 100 percent parts coverage, no manufacturer labor coverage.

    - Manufacturer's Enhanced Warranty with manufacturer Start-up; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - As-available Field Service response; no committed response time.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

    - Manufacturer's Enhanced Warranty with manufacturer Start-up; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - Upgrade from as-available Field Service response to 72-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

    - Manufacturer's Enhanced Warranty with manufacturer Start-up; coverage to include items listed under manufacturer's standard warranty with manufacturer start-up above, plus the following upgrades:

      - Manufacturer Lighting Control System Components, Except Lighting Management System Computer, Ballasts/Drivers and Ballast Modules:

        - First Two Years:

          - Upgrade from as-available Field Service response to 24-hour on-site or remote response time.

          - Plus annual scheduled Preventive Maintenance Visit.

        - Additional Coverage for Years 3-5: 50 percent replacement parts coverage, no manufacturer labor coverage.

        - Additional Coverage for Years 6-8: 25 percent replacement parts coverage, no manufacturer labor coverage.

- PRODUCTS

  - MANUFACTURERS

    - Basis of Design Manufacturer: Lutron Electronics Company, Inc; Quantum System.

    - Other Acceptable Manufacturers:

      - <Insert manufacturer’s name>.

      - Products by listed manufacturers are subject to compliance with specified requirements and prior approval of Engineer.

    - Substitutions: See Section 01 6000 - Product Requirements.

      - All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by Engineer a minimum of 10 working days prior to the bid date and must be made available to all bidders. Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

      - By using pre-approved substitutions, Contractor accepts responsibility and associated costs for all required modifications to related equipment and wiring. Provide complete engineered shop drawings (including power wiring) with deviations from the original design highlighted in an alternate color for review and approval by Engineer prior to rough-in.

    - Source Limitations: Furnish products produced by a single manufacturer and obtained from a single supplier.

  - DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS

    - Sensor Layout and Tuning.

      - Contractor to utilize Lighting Control Manufacturer Installation Instructions to place/install sensors.

      - At Pre-wire and Startup, Lighting Control Manufacturer to provide a rough sensor calibration only. Sensor fine-tuning to be the responsibility of Contractor.

    - Provide products listed, classified, and labeled by Underwriter's Laboratories Inc. (UL) as suitable for the purpose indicated.

    - Unless specifically indicated to be excluded, provide all required equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, software, system programming, etc. as necessary for a complete operating system that provides the control intent indicated.

    - Shade Control Requirements:

      - Capable of operating shades and recalling shade presets via keypad, contact closure input, infrared receiver, lighting management system software, or other lighting control system interface.

      - Capable of operating any individual, group, or subgroup of shade electronic drive units within system without requiring separate group controllers.

      - Capable of assigning and reassigning individual, groups, and subgroups of shades to any control within system without requiring additional wiring or hardware changes.

      - Capable of controlling shade speed for tracking within plus or minus 0.125 inch throughout entire travel.

      - Provide 10 year power failure memory for preset stops, open and close limits, shade grouping and sub grouping and system configuration.

      - Capable of synchronizing multiple shade electronic drive units of the same size to start, stop and move in unison.

      - Capable of stopping shades within accuracy of 0.125 inch at any point between open and close limits.

      - Capable of storing up to 250 programmable stop points, including open, close, and any other position.

      - Capable of controlling lights and shades from single wall control button.

    - Design lighting control equipment for 10 year operational life while operating continually at any temperature in an ambient temperature range of 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C) and 90 percent non-condensing relative humidity.

    - Electrostatic Discharge Tolerance: Design and test equipment to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

    - Dimming and Switching (Relay) Equipment:

      - Designed so that electrolytic capacitors operate at least 36 degrees F (20 degrees C) below the capacitor's maximum temperature rating when the device is under fully loaded conditions at maximum rated temperature.

      - Inrush Tolerance:

        - Utilize load-handling thyristors (SCRs and triacs), field effect transistors (FETs) and isolated gate bipolar transistors (IGBTs) with maximum current rating at least two times the rated operating current of the dimmer/relay.

        - Capable of withstanding repetitive inrush current of 50 times the operating current without impacting lifetime of the dimmer/relay.

      - Surge Tolerance:

        - Panels: Designed and tested to withstand surges of 6,000 V, 3,000 amps according to IEEE C62.41.2 and IEC 61000-4-5 without impairment to performance.

        - Other Power Handling Devices: Designed and tested to withstand surges of 6,000 V, 200 amps according to IEEE C62.41.2 without impairment to performance.

      - Power Failure Recovery: When power is interrupted and subsequently restored, within 3 seconds lights to automatically return to same levels (dimmed setting, full on, or full off) as prior to power interruption.

      - Dimming Requirements:

        - Line Noise Tolerance: Provide real-time cycle-by-cycle compensation for incoming line voltage variations including changes in RMS voltage (plus or minus 2 percent change in RMS voltage per cycle), frequency shifts (plus or minus 2 Hz change in frequency per second), dynamic harmonics, and line noise.

          - Systems not providing integral cycle-by-cycle compensation to include external power conditioning equipment as part of dimming system.

        - Incorporate electronic "soft-start" default at initial turn-on that smoothly ramps lights up to the appropriate levels within 0.5 seconds.

        - Utilize air gap off to disconnect the load from line supply.

        - Control all light sources in smooth and continuous manner. Dimmers with visible steps are not acceptable.

        - Load Types:

          - Assign a load type to each dimmer that will provide a proper dimming curve for the specific light source to be controlled.

          - Provide capability of being field-configured to have load types assigned per circuit.

        - Minimum and Maximum Light Levels: User adjustable on a circuit-by-circuit basis.

        - Line Voltage Dimmers:

          - Dimmers for Magnetic Low Voltage (MLV) Transformers:

            - Provide circuitry designed to control and provide a symmetrical AC waveform to input of magnetic low voltage transformers per UL 1472.

            - Dimmers using unipolar load current devices (such as FETs or SCRs) to include DC current protection in the event of a single device failure.

          - Dimmers for Electronic Low Voltage (ELV) Transformers: Operate transformers via reverse phase control. Alternately, forward phase control dimming may be used if dimming equipment manufacturer has recommended specific ELV transformers being provided.

          - Dimmers for Neon and Cold Cathode Transformers:

            - Magnetic Transformers: Listed for use with normal (low) power factor magnetic transformers.

            - Electronic Transformers: Must be supported by the ballast equipment manufacturer for control of specific ballasts being provided.

        - Low Voltage Dimming Modules:

          - Coordination between Low Voltage Dimming Module and Line Voltage Relay:  Capable of being electronically linked to a single zone.

          - Single low voltage dimming module; capable of controlling the following light sources:

            - 0-10V analog voltage signal.

              - Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

              - Sink current according to IEC 60929.

              - Source current.

            - 10-0V reverse analog voltage signal.

            - DSI digital communication.

            - DALI broadcast communication per IEC 60929:

              - Logarithmic intensity values complying with IEC 60929.

              - Linear intensity values for use with LED color intensity control.

            - PWM per IEC 60929.

      - Switching Requirements:

        - Rated Life of Relays: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - Switch load in a manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

        - Provide output fully rated for continuous duty for inductive, capacitive, and resistive loads.

    - Device Finishes:

      - Wall Controls:

      - Standard Colors: Comply with NEMA WD1 where applicable.

      - Color Variation in Same Product Family: Maximum delta E of 1, CIE L*a*b color units.

      - Visible Parts: Exhibit ultraviolet color stability when tested with multiple actinic light sources as defined in ASTM D4674. Provide proof of testing upon request.

    - Interface with building automation system as specified in Section 27 4113.

  - POWER PANELS

    - Provide power panels with configurations as indicated on the drawings.

    - General Requirements:

      - Listed to UL 508 as industrial control equipment.

      - Comply with UL 508A and IEC 60669-2-1 as applicable.

      - Delivered and installed as a listed factory-assembled panel.

      - Field wiring accessible from front of panel without removing dimmer assemblies or other components.

      - Passively cooled via free-convection, unaided by fans or other means.

      - Shipped with each dimmer in mechanical bypass position by means of jumper bar inserted between input and load terminals. Jumpers to carry full rated load current and be reusable at any time. Mechanical bypass device to allow for switching operation of connected load with dimmer removed by means of circuit breaker.

      - Provided with branch circuit protection for each input circuit unless the panel is a dedicated feed-through type panel or otherwise indicated on the drawings.

      - Branch Circuit Breakers:

        - Listed to UL 489 as molded case circuit breaker for use on lighting circuits.

        - Provided with visual trip indicator.

        - Provide circuit breakers with interrupting capacity as required to provide the short circuit current rating.

          - 10,000 rms symmetrical amperes at 120 VAC.

          - 14,000 rms symmetrical amperes at 277 VAC for dimming.

          - 18,000 rms symmetrical amperes at 277 VAC for switching.

        - Thermal-magnetic construction for overload, short-circuit, and over-temperature protection. Use of breakers without thermal protection requires dimmers/relays to have integral thermal protection to prevent failures when overloaded or ambient temperature is above rating of panel.

        - Equipped with provision for tag-out/lock-out devices to secure circuit breakers in off position when servicing loads.

        - Replaceable without moving or replacing dimmer/relay assemblies or other panel components.

        - Listed as switch duty (SWD) so that loads can be switched on and off by breakers.

      - Provide panels with listed short circuit current rating not less than the available fault current at the installed location as indicated on the drawings.

        - Minimum Short Circuit Current Rating (SCCR): 25,000 A; 45,000 A; 65,000 A.

      - Panel Processor; Circuit Selector:

        - Provide the following capabilities:

          - Operate circuit directly from panel processor for system diagnostics and provide feedback of system operation.

          - Electronically assign each circuit to any zone in lighting control system.

          - Determine normal/emergency function of panel and set emergency lighting levels.

        - Where indicated on the drawings, panels to provide two control links. Each circuit to be capable of transferring control based on independent programming between architectural control system and theatrical controls utilizing the USITT DMX-512 1990 or ESTA DMX-512A protocol.

        - React to changes from control within 20 milliseconds.

      - Diagnostics and Service:

        - Replacing dimmer/relay does not require re-programming of system or processor.

        - Include diagnostic LEDs for dimmers/relays to verify proper operation and assist in system troubleshooting.

        - Include tiered control scheme for dealing with component failure that minimizes loss of control for occupant.

          - If lighting control system fails, lights to remain at current level. Panel processor provides local control of lights until system is repaired.

          - If panel processor fails, lights to remain at current level. Circuit breakers can be used to turn lights off or to full light output, allowing non-dim control of lights until panel processor is repaired.

          - If dimmer fails, factory-installed mechanical bypass jumpers to allow each dimmer to be mechanically bypassed. Mechanical bypass device to allow for switching operation of connected load with dimmer removed by means of circuit breaker.

    - Product(s):

      - Specification Grade Dimming Panels:

        - Product: GP Series Dimming Panels.

        - Mounting: Surface.

        - Dimmers designed and tested specifically to control incandescent/tungsten, magnetic low voltage, electronic low voltage, neon/cold cathode, fluorescent dimming ballasts, and non-dim loads.

        - Unless otherwise indicated or required, utilize universal 16 A continuous-use listed dimmers.

        - For loads requiring 0-10V, PWM, or DSI control, utilize compatible multiple load type low voltage dimming modules.

        - Limit current rise time to minimum 350 microseconds as measured from 10 to 90 percent of load current waveform and minimum 525 microseconds as measured from 0 to 100 percent of load current waveform at 50 percent rated dimmer capacity at a 90 degree conduction angle. Current rise time to be minimum 400 microseconds as measured from 10 to 90 percent of load current waveform and minimum 600 microseconds as measured from 0 to 100 percent of load current waveform at 100 percent rated dimmer capacity at a 90 degree conduction angle.

        - Load faults only affect the given circuit.

      - Modular Dimming Panels:

        - Product: LP Series Dimming Panels.

        - Provide surface-mounted or flush-mounted enclosures as indicated.

        - Unless otherwise indicated or required, utilize multiple load type 16 A feed continuous-use listed dimming/switching modules.

        - For switching only circuits, utilize relays rated for minimum of 1,000,000 cycles at fully rated current for all lighting loads.

        - For loads requiring 0-10V, PWM, or DSI control, utilize compatible multiple load type low voltage dimming modules.

      - Modular Combination Panels:

        - Product: CCP Series Custom Combination Panels.

        - Provide surface-mounted or flush-mounted enclosures as indicated.

        - Unless otherwise indicated or required, utilize multiple load type 16 A feed continuous-use listed dimming/switching modules.

        - For switching only circuits, utilize relays rated for typical 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - For loads requiring 0-10V, PWM, or DSI control, utilize compatible multiple load type low voltage dimming modules.

      - Relay Panels:

        - Product:  XP Series Switching Panels.

        - Provide surface-mounted or flush-mounted enclosures as indicated.

        - Switching Requirements:

          - Utilize 20 A continuous-use rated switching modules; able to switch 20 A receptacles.

          - Rated Life of Relay: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

          - Switch load in a manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

          - Provide output fully rated for continuous duty for inductive, capacitive, and resistive loads.

      - DC Dimming Panels:

        - Product: DCI Series Dimming Panels.

        - Mounting: Surface.

        - Meet recommended electrical noise levels of MRI system manufacturers.

        - Operate lamps free from audible noise and flicker throughout entire dimming range.

        - In case of control system failure, supervisory circuit to shut down power to load.

        - Automatically detect and compensate for lamp failures to maintain consistent DC voltage level.

  - FLUORESCENT ELECTRONIC DIMMING BALLASTS

    - General Requirements:

      - Designed for 10 year operational life while operating at maximum case temperature and 90 percent non-condensing relative humidity.

      - Designed and tested to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

      - Lamp Starting Method: Programmed rapid start.

      - Maximum Inrush Current: 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

      - Current Crest Factor (CCF): Less than 1.7.

      - Comply with ANSI C82.11 and list and label as complying with UL 935.

      - Designed to not interfere with infrared devices operating at frequencies between 38 kHz and 42 kHz.

      - Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.

      - Inaudible in a 27 dBA ambient.

      - No visible change in light output with a variation of plus or minus 10 percent line voltage input.

      - Actively prevent overheating in T5-HO linear fluorescent lamp applications.

      - Ballasts to track evenly across multiple lamp lengths and all light levels.

      - Comply with IEC 61347-2-3 as applicable.

    - 3-Wire Control:

      - Provide integral fault protection to prevent ballast failure in the event of a mis-wire.

    - Digital Control:

      - Monitor and report lamp and ballast status.

      - Lights automatically return to the setting prior to power interruption.

      - Each ballast responds independently to:

        - Up to 32 occupant sensors.

        - Up to 64 personal control inputs.

        - Two daylight sensors.

      - Unique internal reference number visibly displayed on ballast cover.

      - Averages two independent daylight harvesting inputs internally.

      - Responds to digital load shed command. (Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by three percent to 27 percent).

    - Product(s):

      - 3-Wire Control, One Percent Dimming; Hi-lume:

        - Dimming Range: 100 percent to one percent relative light output for T4 compact and T5-HO lamps.

        - Surge Tolerance: Designed and tested to withstand Category A surges of 6,000 V according to IEEE C62.41.2 without impairment of performance.

        - Total Harmonic Distortion (THD): Less than 10 percent.

      - 3-Wire and Digital Control, One Percent Dimming; Hi-lume 3D:

        - Dimming Range: 100 percent to less than one percent relative light output for T8, T5 and T5HO, and five percent relative light output for T5 twin-tube lamps.

        - Surge Tolerance: Designed and tested to withstand Category A surges of 6,000 V according to IEEE C62.41.2 without impairment of performance.

        - Total Harmonic Distortion (THD): Less than 10 percent typical (15 percent for select models).

      - 3-Wire and Digital Control, Ten Percent Dimming; EcoSystem:

        - Dimming Range: 100 to ten percent relative light output for T8, T5, T5HO, and T5 twin-tube, and five percent relative light output for T4 compact lamps.

        - Surge Tolerance: Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

        - Total Harmonic Distortion (THD): Less than 10 percent typical (15 percent for select models).

        - Digital Control:

          - Connect without interface (except for T4 compact lamp ballasts) to:

            - Occupancy sensors.

            - Daylight sensor.

            - Personal control input (keypad or infrared receiver).

          - Provide a 20V DC source to power connected sensors.

          - Generate digital communication commands to distribute ballast and sensor data on the digital bus.

      - Digital Control, One Percent Dimming; EcoSystem H-Series:

        - Dimming Range: 100 to less than one percent relative light output for T8, and one percent relative light output for T5 and T5HO lamps.

        - Surge Tolerance: Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

        - Total Harmonic Distortion (THD): Less than 10 percent typical (15 percent for select models).

  - LED DRIVERS

    - General Requirements:

      - Designed for 10 year operational life while operating at maximum case temperature and 90 percent non-condensing relative humidity.

      - Designed and tested to withstand electrostatic discharges without impairment when tested according to IEC 61000-4-2.

      - UL 8750 recognized or listed as applicable.

      - Complies with IEC 61347-2-13 as applicable.

      - Surge Tolerance: Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.

      - Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.

      - Class A sound rating; Inaudible in a 27 dBA ambient.

      - No visible change in light output with a variation of plus or minus 10 percent line voltage input.

      - Total Harmonic Distortion (THD): Less than 20 percent for loads greater than 25W; comply with ANSI C82.11.

      - Drivers to track evenly across multiple lamp lengths and all light levels.

      - Configuration tool available to optimize the following for LED fixtures:

        - Light level.

        - Efficacy.

        - Thermal performance.

    - 3-Wire Control:

      - Provide integral fault protection to prevent driver failure in the event of a mis-wire.

      - Operate from input voltage of 120 V through 277 V at 60 Hz.

    - Digital Control:

      - Lights automatically return to the setting prior to power interruption.

      - Operate from input voltage of 120 V through 277 V at 60 Hz.

      - Each driver responds independently to:

        - Up to 32 occupant sensors.

        - Up to 16 daylight sensors.

      - Responds to digital load shed command. (Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by three percent to 27 percent).

    - Product(s):

      - Forward Phase (Neutral Wire Required), 3-Wire, and Digital Control, One Percent Dimming; A-Series:

        - Dimming Range:  100 to one percent relative light output.

        - Maximum Inrush Current: 2 amperes for 120V and 277V drivers.

        - Constant Current Drivers:

          - Support from 200 mA to 2.1 A (in 10 mA steps) to ensure a compatible driver exists.

          - Support LED arrays up to 40W or 53 W (710 mA to 1.05 A in 10 mA steps).

        - Constant Voltage Drivers:

          - Support from 10 V to 60 V (in 0.5 V steps) to ensure a compatible driver exists.

          - Support LED arrays up to 40W.

        - Dimming Range:  100 to five percent relative light output.

        - Maximum Inrush Current: Meets NEMA 410 inrush requirements.

        - Constant Current Drivers:

          - Support from 220 mA to 1.4 A to ensure a compatible driver exists.

          - Support LED arrays up to 60W.

  - POWER INTERFACES

    - Provide power interfaces as indicated or as required to control the loads as indicated.

    - General Requirements:

      - Phase independent of control input.

      - Rated for use in air-handling spaces as defined in UL 2043.

      - Utilize air gap off to disconnect the load from line supply.

      - Diagnostics and Service: Replacing power interface does not require re-programming of system or processor.

    - Product(s):

      - Phase-Adaptive Power Module; PHPM-PA:  Provides interface for phase control input to provide full 16 A circuit output of forward/reverse phase control for compatible loads.

      - 3-Wire Fluorescent Power Module; PHPM-3F:  Provides interface for phase control input to provide full 16 A circuit output for compatible line-voltage control fluorescent electronic dimming ballasts.

      - Switching Power Module; PHPM-SW: Provides interface for phase control input to provide full 16 A circuit output of switching for compatible non-dim loads.

      - Phase-Adaptive Power Module with 3-Wire Fluorescent Input; PHPM-WBX: Provides interface for fluorescent ballast control input to provide full 16 A circuit output for compatible loads.

      - Ten Volt Interface; GRX-TVI: Provides interface for phase control input to provide full 16 A circuit output of switching and 0-10 V low voltage control for compatible fluorescent electronic dimming ballasts.

  - MAIN UNITS

    - Product: GRAFIK Eye QS.

    - Provide main units with configuration and quantity of zones as indicated or as required to control the loads as indicated.

    - Connects to lighting management hub via RS485.

    - Finish: As specified for wall controls in "Device Finishes" under DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above.

    - Engrave units with button, zone, and scene descriptions to be selected by Engineer or Owner.

    - Integrated Wireless Capability:

      - Provide wireless communication inputs for:

        - Occupancy sensors.

        - Daylight sensors.

        - Wireless controller.

      - RF Range: 30 feet (9 m) between sensor and compatible RF receiving device(s).

      - RF Frequency: 434 MHz; operate in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

    - Preset Lighting Control with Zone Override:

      - Intensity for each zone indicated by means of one illuminated bar graph per zone.

      - User-programmable zone and scene names.

      - Utilize air gap off to disconnect the load from line supply.

      - Astronomical time clock and programmer interface provides access to:

        - Scene selections.

        - Fade zone to a level.

        - Fine-tuning of preset levels with scene raise/lower.

        - Lock out scenes and zones.

        - Fine-tuning of light levels with individual zone raise/lower.

        - Terminal block for wired infrared signal input.

        - Enable/disable wall station.

      - Light intensity with real time energy savings by digital display.

      - Fade time indicated by digital display for current scene while fading.

      - Integral wide angle infrared receiver.

      - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

      - Direct Low-Voltage Control of Digital Ballasts and LED drivers (120V, 220/240V, 277V and/or 347V Lighting):

        - Electronically link a digital fluorescent lighting ballast to a zone for both dimming and turning on/off.

        - Electronically assign daylight sensors to digital ballasts and line voltage dimmers for proportional daylight harvesting.

        - Single integral controller with Class 1 or Class 2 isolated digital output signal conforming to IEC 60929; capable of direct control without interface.

      - Creates daylighting rows independent of control zones.

      - Capable of re-zoning without re-wiring using programming display on unit.

      - Outputs can be virtually mapped to other device's outputs.

      - Zone raise/lower buttons capable of controlling local lighting loads connected to the main unit or remote lighting zones in the system.

    - Preset Shade Control with Zone Override:

      - Preset expandable shade control: Provide up to three columns of shade control.

      - For temporary local overrides, individual raise/lower buttons to allow zones to be adjusted without altering scene values stored in memory.

    - Provides one direct-wired occupancy sensor connection without interface or power pack.

  - LIGHTING CONTROL MODULES

    - Provide lighting control modules as indicated or as required to control the loads as indicated.

    - General Requirements:

      - Listed to UL 508 as industrial control equipment.

      - Delivered and installed as a listed factory-assembled panel.

      - Passively cooled via free-convection, unaided by fans or other means.

      - Mounting: Surface.

      - Connection without interface to wired:

        - Occupancy sensors.

        - Daylight sensors.

        - IR receivers for personal control.

      - Connects to lighting management hub via RS485.

      - LED status indicators confirm communication with occupancy sensors, daylight sensors, and IR receivers.

      - Contact Closure Input:

        - Directly accept contact closure input from a dry contact closure or sold-state output without interface to:

          - Activate scenes.

            - Scene activation from momentary or maintained closure.

          - Enable or disable after hours.

            - Automatic sweep to user-specified level after user-specified time has elapsed.

            - System will provide occupants a visual warning prior to sweeping lights to user-specified level.

            - Occupant can reset timeout by interacting with the lighting system.

          - Activate or deactivate demand response (load shed).

            - Load shed event will reduce lighting load by user-specified amount.

      - Emergency Contact Closure Input:

        - Turn all zones to full output during emergency state via direct contact closure input from UL 924 listed emergency lighting interface, security system or fire alarm system.

        - Allow configurable zone response during emergency state.

        - Disable control operation until emergency signal is cleared.

      - Supplies power for control link for keypads and control interfaces.

      - Distributes sensor data among multiple lighting control modules.

      - Capable of being controlled via wireless sensors and controls.

    - Switching Lighting Control Modules:

      - Product(s):

        - SoftSwitch Energi Savr Node; Model QSN-4S16-S:  16 A continuous-use per channel.

        - SoftSwitch Energi Savr Node; Model QSN-4S20-S:  20 A (16 A ballast) continuous-use per channel.

      - Switching:

        - Rated Life of Relay: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

        - Fully rated output continuous duty for inductive, capacitive, and resistive loads.

        - Module to integrate up to four individually controlled zones.

        - Utilize air gap off, activated when user selects "off" at any control to disconnect the load from line supply.

    - 0-10V Lighting Control Modules:

      - Product(s):

        - 0-10V Energi Savr Node; Model QSN-4T16-S:  16 A continuous-use per channel.

        - 0-10V Energi Savr Node; Model QSN-4T20-S:  20 A (16 A ballast) continuous-use per channel.

      - Coordination Between Low Voltage Dimming Module and Line Voltage Relay: Capable of being electronically linked to single zone.

      - Single low voltage dimming module; capable of controlling following light sources:

        - 0-10V analog voltage signal.

          - Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

          - Sink current per IEC 60929.

        - 10V-0V analog voltage signal.

          - Provide Class 2 isolated 0-10V output signal conforming to IEC 60929.

          - Sink current per IEC 60929.

      - Switching:

        - Rated Life of Relay: Typical of 1,000,000 cycles at fully rated 16 A for all lighting loads.

        - Load switched in manner that prevents arcing at mechanical contacts when power is applied to and removed from load circuits.

        - Fully rated output continuous duty for inductive, capacitive, and resistive loads.

        - Module to integrate up to four individually controlled zones.

        - Utilize air gap off, activated when user selects "off" at any control to disconnect the load from line supply.

    - Digital Fixture Lighting Control Modules:

      - Product(s):

        - EcoSystem Energi Savr Node; Model QSN-1ECO-S: One EcoSystem Digital Link.

        - EcoSystem Energi Savr Node; Model QSN-2ECO-S: Two EcoSystem Digital Links.

      - Provides two-way feedback with digital fixtures for energy monitoring, light level status, lamp failure reporting, and ballast/driver failure reporting.

      - Provide testing capability using manual override buttons.

      - Each low-voltage digital communication link to support up to 64 ballasts or LED drivers capable of NFPA 70 Class 1 or Class 2 installation.

    - Total Light Management Control Module (Digital Lighting and Shades Control):

      - Product: EcoSystem with Shades Energi Savr Node; Model QSN-2ECO-PS120 - Two EcoSystem Digital Links.

      - Ten fused 30W (60W peak) 24V DC outputs provide power to compatible shades, drapery drive units, keypads, and accessories.

      - Provide power for 10 to 30 shades dependent on shade dimensions.

      - Provide smart diagnostics for system verification.

      - Provide testing capability using manual override buttons.

      - Each low-voltage digital communication link to support up to 64 ballasts capable of NFPA 70 Class 1 or Class 2 installation.

  - ENERGY METER

    - Product: Quantum CPN5898 Series Class 500 Energy Meter.

    - General Requirements:

      - Provides accurate, real-time energy metering and verification capability through front-end PC-based software.

      - Factory-calibrated; not requiring preventative/scheduled maintenance or cleaning/decontamination procedures.

      - Accepts up to three sets of current sensors to monitor up to three loads of the same voltage with one meter.

      - Contains direct-read 8-digit LCD display of cumulative kWh.

      - Current Sensors: Split-core; capable of being placed up to 500 feet (152 m) from the meter without power interruption.

      - Connects to server via Ethernet.

      - UL listed.

      - Accuracy: Plus/minus 0.5 percent, certified to ANSI C12.20.

      - NEMA 12 housing.

      - Provide voltage and current ratings suitable for the installed location.

  - DIGITAL DIMMING BALLAST AND SWITCHING MODULES

    - Provide digital dimming ballast and switching modules as indicated or as required to control the loads as indicated.

    - General Requirements:

      - Provide continuous 3-wire signal dimming to compatible 3-wire electronic dimming ballasts.

      - Utilize air gap off to disconnect the load from line supply.

      - Connect without interface to:

        - Occupancy sensor.

        - Daylight sensor.

        - Personal control input (wall station or infrared receiver).

      - Generate digital communication commands to distribute ballast and sensor data on the digital bus.

      - If power is interrupted and subsequently restored, lights automatically return to the setting prior to power interruption.

      - Each ballast module responds independently to:

        - Up to 32 occupancy sensors.

        - Up to 64 personal control inputs.

        - Two daylight sensors.

      - Unique internal reference number visible displayed on module cover.

      - Averages two independent daylight harvesting inputs internally.

      - Responds to digital load shed command.

        - Sets high end trim.

        - Automatically scales light output proportional to load shed command. (Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast to automatically set the maximum light output at 90 percent and lower current light output by 3 percent to 27 percent).

      - Provide integral fault protection to prevent ballast module failure in the event of a mis-wire.

    - Product(s):

      - 3-Wire Ballast Module, 2 Amp; EcoSystem Model C5-BMF-2A:

        - Integrates up to 2 amps of 3-wire electronic dimming ballasts into EcoSystem digital control system as a single zone.

      - 3-Wire Ballast Module, 16 Amp; EcoSystem Model C5-BMJ-16A:

        - Integrates up to 16 amps of 3-wire electronic dimming ballasts into EcoSystem digital control system as a single zone.

        - Integrates up to 16 amps of switched high intensity discharge (HID) lighting load into EcoSystem digital control system as a single zone.

      - Switching Power Module, 16 Amp; EcoSystem Model C5-XPJ-16A:

        - Integrates up to 16 amps of high in-rush lighting load (magnetic fluorescent ballast, electronic fluorescent ballast, HID, incandescent, magnetic low-voltage, electronic low-voltage, neon/cold cathode and motor loads) into EcoSystem digital control system as a single zone.

  - LIGHTING MANAGEMENT HUBS

    - Product: Quantum Light Management Hub.

    - Provided in a pre-assembled NEMA listed enclosure with terminal blocks listed for field wiring.

    - Connects to controls and power panels via RS485.

    - Enables light management software to control and monitor compatible dimming ballasts and ballast modules, power panels, power modules, and window treatments.

      - Utilizes Ethernet connectivity to light management computer utilizing one of the following methods:

        - Dedicated network.

        - Dedicated VLAN.

        - Shared network with Building Management System (BMS).

        - Corporate network where managed switches are configured to allow multicasting and use of IGMP.

    - Integrates control station devices, power panels, shades, preset lighting controls, and external inputs into a single customizable lighting control system with:

      - Multiple Failsafe Mechanisms:

        - Power failure detection via emergency lighting interface.

        - Protection: Lights go to full on if ballast wires are shorted.

        - Distributed architecture provides fault containment. Single hub failure or loss of power does not compromise lights and shades connected to other lighting management hubs.

      - Manual overrides.

      - Automatic control.

      - Central computer control and monitoring.

      - Integration with BMS via BACnet.

    - Furnished with astronomical time clock.

    - Furnished with solar clock to track the position of the sun to control the shades to limit penetration of direct sunlight.

    - Maintains a backup of the programming in a non-volatile memory capable of lasting more than ten years without power.

    - BACnet Integration License:

      - Provide ability to communicate by means of native BACnet IP communication (does not require interface) to lighting control system from a user-supplied 10BASE-T or 100BASE-T Ethernet network.

      - Requires only one network connection per system.

      - Lighting control system to be BACnet Test Laboratory (BTL) listed.

      - Basic BACnet integration license:

        - The BACnet integrator can command:

          - Area light output.

          - Area enable or disable after hours mode.

          - Area load shed level.

          - Area load shed enable/disable.

          - Area shade group presets and levels.

          - Enable/Disable:

            - Automated solar adaptive shade control.

            - Cloudy day/shadow override mode for automated shade control.

            - Brightness override mode for automated shade control.

            - Area occupancy sensors.

            - Area daylighting.

          - Daylighting level.

          - Area occupied and unoccupied level

          - Occupancy sensor timeouts.

        - The BACnet integrator can monitor:

          - Area on/off status.

          - Area occupancy status.

          - Area fault.

            - Lamp failures.

            - Control devices not responding.

          - Area load shed status.

          - Area instantaneous energy usage and maximum potential power usage.

          - Energy savings broken out by strategy (occupancy, timeclock, daylighting, personal control, tuning, load shed) down to the individual area.

          - Area shade group presets and levels.

          - Cloudy day and shadow sensor status.

          - Light levels from window mounted sensors.

          - Enable/Disable:

            - Status of automated solar adaptive shade control.

            - Status of cloudy day/shadow override for automated shade control.

            - Status of brightness override for automated shade control.

            - Area occupancy sensors.

            - Daylighting.

          - Daylighting level.

          - Light levels from photo sensors and window mount shadow sensors.

          - Area occupied and unoccupied level.

          - Occupancy sensor timeouts.

        - Shade assignment and grouping to be discoverable with third party building management software.

  - LIGHTING MANAGEMENT SYSTEM COMPUTERS

    - No computers to be provided. Lighting Control System Manufacturer authorized Service Representative to perform system start-up without on-site computer.

    - Computers:

      - Product: Q-Manager.

      - System PC (Desktop/Laptop):

        - Suitable for occasional programming, monitoring, and control of digital network lighting controls.

        - Unless otherwise indicated, computer(s) to be provided by lighting control system manufacturer.

        - Quantity:  Provide allowance for 1 computer.

        - Location: As directed by Owner.

        - Minimum Hardware Requirements:

          - Processor: Single Intel® Xeon® processor with minimum speed of 2.0 GHz.

          - 1 GB RAM.

          - 80 GB hard drive (30 GB for application).

          - One 10/100/1000 Ethernet network interface for communication with lighting management hubs.

          - 17 inch (43 cm) monitor with 1024 x 768 resolution.

          - 48X CD/DVD-ROM drive.

          - 4 USB 2.0 ports.

        - Minimum Software Requirements:

          - Licensed installation of US English 32-bit or 64-bit Microsoft® Windows® Server 2008 with Service Pack 1.

      - Server:

        - Suitable for 24 hour per day, 7 day per week programming, monitoring, control, and data logging of digital-network lighting controls.

        - Suitable to handle client machine request in multi-computer systems.

        - Unless otherwise indicated, computer to be provided by lighting control system manufacturer.

        - Minimum Hardware Requirements:

          - Processor: Single Intel® Xeon® processor with minimum speed of 2.0 GHz.

          - 2 GB Ram.

          - 80 GB hard drive (30 GB for application).

          - Two 10/100/1000 Ethernet network interfaces - one for communication with lighting management hubs and one for communication with corporate intranet to allow access from system PCs and/or energy saving display terminals. Only one Ethernet network interface is required if all lighting management hubs and client PCs are on the same network.

          - 17 inch (43 cm) monitor with 1024 x 768 resolution.

          - 48X CD/DVD-ROM drive.

          - 4 USB 2.0 ports.

        - Minimum Software Requirements:

          - Licensed installation of US English 32-bit or 64-bit Microsoft® Windows® Server 2008 with Service Pack 1.

      - Energy Savings Display (GreenGlance) Terminals:

        - Suitable for displaying energy savings data on user-supplied display.

        - Unless otherwise indicated, computer(s) to be provided by others.

        - Quantity: To be determined.

        - Location(s): As directed by Owner.

        - Minimum Hardware Requirements:

          - Processor: Single Intel® Xeon® processor with minimum speed of 2.0 GHz.

          - 1 GB RAM.

          - 80 GB hard drive (30 GB for application).

          - One 10/100/1000 Ethernet network interface for communication with lighting management hubs.

          - 17 inch (43 cm) monitor with 1024 x 768 resolution.

          - 48X CD/DVD-ROM drive.

          - 4 USB 2.0 ports.

        - Minimum Software Requirements:

          - Licensed installation of US English 32-bit or 64-bit Microsoft® Windows® Server 2008 with Service Pack 1.

      - Computers Provided by Lighting Control System Manufacturer: Computer software to be preinstalled and tested prior to shipping.

  - LIGHTING MANAGEMENT SYSTEM SOFTWARE

    - Provide system software license and hardware that is designed, tested, manufactured, and warranted by a single manufacturer.

    - Configuration Setup Software:

      - Product:   Q-Design.

      - Suitable to make system programming and configuration changes.

      - Windows-based, capable of running on either central server or a remote client over TCP/IP connection.

      - Allows manufacturer (either remotely or with on-site service call) or end-user (with training) to:

        - Capture system design:

          - Geographical layout.

          - Load schedule zoning.

          - Shade grouping.

          - Equipment schedule.

          - Equipment assignment to lighting management hubs.

          - Daylighting design.

        - Define the configuration for the following in each area:

          - Lighting scenes.

          - Shade group presets.

          - Control station devices.

          - Interface and integration equipment.

          - Occupancy/after hours.

          - Partitioning.

          - Daylighting.

          - Emergency lighting.

          - Night lights.

        - Startup:

          - Addressing.

          - Daylighting.

          - Provide customized conditional programming.

    - Control and Monitor Software:

      - Products:

        - Quantum Vue (web-based application).

        - Q-Admin (desktop application).

      - Accessibility and Platform Support:

        - Quantum Vue Web-Based Application:

          - Web-based; runs on most HTML5 compatible browsers (including Internet Explorer, Chrome, and Safari).

          - Supports multiple platforms and devices; runs from a tablet, desktop, laptop, or smartphone; optimized for displays of 1024 by 768 pixels or higher.

          - User interface supports multi-touch gestures such as pinch to zoom, drag to pan, etc.

          - Utilizes HTTPS (industry-standard certificate-based encryption and authentication for security).

        - Q-Admin Desktop Application:

          - Client installation for Windows-based operating systems only.

      - System Navigation and Status Reporting:

        - Quantum Vue Web-Based Application:  Performed using graphical floor plan view or a generic system layout.

          - Graphical Floor Plan View:  Utilizes customized CAD based drawing of the building. Pan and zoom feature allows for easy navigation; dynamically adjusts the details presented based on zoom level.

          - Area, scene, and zone names can be changed in real time.

        - Q-Admin Desktop Application:  Performed using basic system tree view.

      - Control of Lights:

        - Area lights can be monitored for on/off status.

        - All lights in an area can be turned on/off or sent to a specific level.

        - For areas that have been zoned, these areas may be sent to a predefined lighting scene, and individual zones may be controlled.

        - Area lighting scenes can be renamed and modified in real-time, changing the levels that zones go to when a scene is activated.

        - High and low end of area lighting can be tuned/trimmed.

        - Control and monitor area partition status.

      - Control of Shades:

        - Area shades can be monitored for current preset or position.

        - Area shades can be opened/closed, sent to a preset, or sent to a specific position.

      - Occupancy:

        - Area occupancy can be monitored.

        - Area occupancy can be disabled to override occupancy control or in case of occupancy sensor problems.

        - Area occupancy settings including level that lights turn on to when area is occupied, and level that lights turn off to when area is unoccupied can be changed in real-time.

        - Monitor energy savings due to occupancy down to an individual area.

      - Daylighting:

        - Daylighting can be enabled/disabled. Can be used to override the control currently taking place in the space.

        - Daylight calibration can be adjusted for each daylit area.

        - Daylight status can be monitored.

        - Monitor energy savings due to daylight harvesting down to an individual area.

      - Load Shedding; IntelliDemand: Allows the building manager to monitor whole building lighting power usage and apply a customized load shed reduction to selected areas, thereby reducing a building's power usage; load shedding triggered via Quantum software, BACnet, or OpenADR.

      - Scheduling: Schedule time of day and astronomic time clock events to automate functions.

        - Adjust or disable a single occurrence of a repeating scheduled event.

        - Easily monitor and adjust scheduled events using a weekly calendar view.

      - Reporting: Provide reporting capability that allows the building manager to gather real-time and historical information about the system as follows:

        - Energy Reports: Show a comparison of cumulative energy used over a period of time for one or more areas or meter groups.

        - Power Reports: Show power usage trend over a period of time for one or more areas or meter groups.

        - Energy Density Report:  Show energy usage in W/sq ft.

        - Energy Savings By Strategy Report: Show energy savings for any area broken down by strategy (tuning, occupancy, daylighting, scheduled events, personal control, and load shedding).

        - Activity Report: Show what activity has taken place over a period of time for one or more areas. Activity includes occupant activities (e.g. wall controls being pressed), building manager operation (e.g. controlling/changing areas using the control and monitor tool), and device failures (e.g. keypads or ballasts that are not responding).

          - Include shade related activities (e.g. automatic movements from Hyperion automated shade algorithm, manual overrides from personal controls, automatic overrides from sensors).

        - Lamp Failure Report: Shows which areas are currently reporting lamp failures.

        - Shade Level Report: Shows the shade level for any shade group in the system over any historical 24 hour period.

        - Shade Position Report: Shows the percentage of time shade groups in the system are at each position.

        - Sensor Level Report: Shows the light level in footcandles of any photosensor in the system.

        - Alert Activity Report: Capable of generating historical reports of all alert activity within the system.

        - Hyperion Automated Shade Control Activity Report:  A chart that combines multiple data points regarding the position and performance of Hyperion automated shades.

      - Diagnostics: Allows the building manager to check on the status of all equipment in the lighting control system. Devices to be listed with a reporting status of OK, missing, or unknown.

      - Alerts and Alarms: Monitors the system for designated events/triggers and automatically generates alerts according to configured response criteria.

        - Capable of monitoring for the following events/triggers:

          - A failed piece of equipment (e.g. ballast, control, sensor, etc.); alert cleared when equipment is replaced.

          - A lamp outage (for compatible EcoSystem digital electronic dimming ballasts only); alert cleared when lamp is replaced.

          - Low battery conditions in battery-operated sensors and controls; alert cleared when battery is replaced.

          - Luminaires with lamp operating hours in excess of designated time.

          - A load shed event; alert generated for beginning and end of trigger.

          - Energy usage higher than designated threshold target.

          - Potential light level condition discrepancies (daylight sensors not agreeing with expected lighting status).

        - View alerts on a customized graphical floor plan.

        - Capable of generating alerts through visible changes in software or through email messages.

        - Capable of customizing the frequency of alerts and providing notifications immediately or through daily, weekly, or monthly summaries.

        - Capable of sending different alerts to different system users.

        - Capable of generating historical reports of all alert activity within the system.

      - Administration:

        - Users: Allows new user accounts to be created and existing user accounts to be edited.

          - Supports Active Directory (LDAP) tying user accounts to network accounts.

        - Area and feature access can be restricted based on login credentials with three levels of access rights (Admin, Programmer, Controller) and customized access levels available.

        - Publish Graphical Floor Plan: Allows admin user to publish new graphical floor plan files, allowing users to monitor the status of lights, occupancy of areas, and daylighting status.

        - Back-Up Project Database: Allows admin user to back up the project database that holds all the configuration information for the system, including keypad programming, areas scenes, daylighting, occupancy programming, emergency levels, night lights, and time clock.

        - Publish Project Database: Allows admin user to send a new project database to the server and download the new configuration to the system. The project database holds all the configuration information for the system, including keypad programming, area scenes, daylighting, occupancy programming, emergency levels, night lights, and time clock.

      - Favorite Buttons: Provide global scene control or modes of operation across the entire system.

      - Provides control/monitoring of partition status to automatically reconfigure how the space operates based on the partition's open/closed status.

    - Energy Savings Display Software:

      - Product: GreenGlance.

      - Provide software from a single manufacturer that can collect and display real-time and historical energy savings data from all of the components in the lighting control system or from the meters in the system.

      - Energy savings data to be accessible for display on computer terminal or user-supplied display monitor via energy savings display software.

      - Software to be capable of displaying:

        - Current savings in percent and kW.

        - Historic energy savings in kWh saved, money saved, coal not burned, and carbon dioxide not emitted.

        - Historical views in time periods of three hours, one day, one week, one month, and one year.

        - Configurable energy usage baseline and user-defined working hours for energy saving calculations.

        - Comparisons of historical periods (days, weeks, months, years).

        - Local weather conditions.

    - Web Services Integration License:

      - Provide ability to communicate by means of XML web services

      - Web services integrator can monitor:

        - Area instantaneous power usage.

        - Area instantaneous power savings.

        - Area energy savings.

        - Area energy usage.

        - Area maximum power usage.

      - Initiate load shed event using OpenADR protocol in an auto-Demand-Response event without additional interfaces or gateways.

      - Supports both push and pull for integration with third party systems and energy dashboards.

    - Quantum Mobile Control and Programming Software License:

      - Allows mobile control and programming of Quantum system via an Apple iPad.

      - Provides users the ability to:

        - Control and monitor area lighting scenes, zones, and shade presets.

        - Easily identify zones and shade groups.

        - Edit area lighting scenes, shade presets, scene fade rates, and scene delay rates.

        - Restrict user access by area.

        - Restrict users from ability to make changes.

        - Historical logging of who made changes available in Q-Admin control and monitor software.

      - Connects to Quantum system via Wi-Fi.

      - Can connect directly to processor or through computer (server) in the system.

    - Personal Web-Based Control Software:

      - Product: Personna PC.

      - Lighting Control: Allows the user to use a web browser on their personal PC, laptop, or some mobile devices (supporting 1024 by 768 resolution) to control one or more lights in their area.

        - The user may select between full on, full off, or a favorite light level.

        - The user may raise/lower the currently selected lighting level in the area.

      - Shade Control: Allows the user to use a web browser on their personal PC, laptop, or some mobile devices (supporting 1024 by 768 resolution) to control one or more shades in their area.

        - The user may select open, closed, or a favorite shade position.

        - The user may raise/lower a selected shade group in the area.

      - Supports up to 10,000 users.

      - Each user to have a login name and password sent from administrator via email when user account created.

      - Supported Browsers: Microsoft Internet Explorer (versions 7 and higher), Mozilla Firefox (versions 3 and higher), Apple Safari (versions 4 and higher), Google Chrome (versions 8 and higher).

    - Automated Shade Control Software:

      - Product: Hyperion.

      - Objectives:

        - Uses open loop solar adaptive algorithm to minimize the penetration depth of direct sunlight.

        - Optimizes energy savings from daylight.

        - Provides manual override capability for occupants via wall-mounted keypad or simple remote control.

        - Provides automatic override capability utilizing a local sensor in dark conditions or when excessive brightness occurs.

        - Maximizes occupants’ connectivity with outdoors by optimizing view.

        - Provides diffuse daylight and minimizes direct sunlight in the space to reduce solar heat gain and maximize occupant comfort in the space.

        - Reduces glare.

        - Shades along same facade to start, stop and track in unison to maintain a consistent exterior aesthetic.

        - Provides optional presets to allow shades to align with architectural elements of the facade.

        - Provides a preset, also referred to as visor position, to limit maximum amount of light entering a space.

        - Provides configurable dark and bright override positions.

      - Hardware: Independent operation of solar tracking program through non-Windows based operating system provided in one or more lighting management hubs.

      - Control Software:

        - Incorporates a solar tracking software that:

          - Calculates the sun's position in the sky relative to the building and then calculates when shade movement is necessary by facade.

          - Calculates the position of the shade to limit direct sunlight penetration to a predetermined limit.

        - Controlled using the following inputs for startup:

          - Building location.

          - Facade orientation.

          - Window dimensions.

          - Solar depth of penetration.

          - Number of shade movements per day.

          - Visor position of shades.

          - Optional presets that align shades with architectural features of the facade.

          - Light level thresholds for dark and bright override.

          - Shade position for dark and bright override.

          - Window position on wall.

        - Requires minimal long term maintenance and service. Does not require user to make daily changes to programming or overall system functionality, unless desired by owner.

      - PC Graphic User Interface: Provides access to all adjustable parameters of solar depth of penetration and number of shade movements per day.

      - Override:

        - Manual:

          - Temporary override of the control program capability through optional manual keypads, remote controls, or end-user control software.

          - Keypads, remote controls, or end-user control software to be capable of providing manual control of shades in a particular area.

          - Time of manual override to be programmable.

        - Automatic overrides achievable via rooftop cloudy day sensors or radio window sensors:

          - Rooftop Cloudy Day Sensors:

            - Product: Cloudy Day Sensor; Model QS-CES-R.

            - Provides automatic override of system on dark cloudy days.

            - During dark conditions, shades to go to predetermined visor position to maximize view and available daylight.

          - Radio Window Sensors:

            - Product(s):

              - Radio Window Sensor; Model LRF2-SSM-XX (mullion mount sensor pair).

              - Radio Window Sensor; Model LRF2-SSW-WH (window mount).

            - Monitors exterior light conditions and provides automatic override of system on dark cloudy days or in the presence of shadows from neighboring buildings and rooftop mechanical equipment.

            - During dark conditions, shades to go to predetermined dark override position to maximize view and available daylight.

            - Monitors exterior light conditions and provides automatic override of system during excessive brightness.

            - During excessive bright conditions, shades to go to predetermined bright override position to maximize occupant comfort.

            - Capable of having one or multiple sensors per facade for more localized detection of exterior light conditions.

            - Capable of having one sensor control one shade group or multiple shade groups.

            - Software enables the ability to adjust thresholds, timeouts, and shade movement frequency globally or per area to meet the unique preferences of different individuals.

            - Sensor to not require external power packs, power wiring, or communication wiring.

            - Sensor to be easily mountable to mullion (mullion mount sensor pair) or window (window mount) and can be easily removed and repositioned without marring or damaging window surface.

            - Provides typical battery lifetime of 10 years when installed per manufacturer instructions.

            - Communicates directly to compatible Lutron QS sensor module via Lutron Clear Connect Technology to ensure reliable RF communications.

            - RF Frequency: 434 MHz.

            - RF Range: 30 feet (9 m) between sensor and compatible RF receiving device(s).

            - Intuitive test mode to provide instant system verification of associated shades and programmed visor position.

  - CONTROL STATIONS

    - Provide control stations with configuration as indicated or as required to control the loads as indicated.

    - Wired Control Stations:

      - General Requirements:

        - Class 2 (low voltage).

        - UL listed.

        - Control stations can be replaced without reprogramming.

        - Finish: As specified for wall controls in "Device Finishes" under DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above.

      - Product(s):

        - Multi-Scene Wired Control:

          - Product(s):

            - Lutron seeTouch QS.

            - Lutron Signature Series.

            - Lutron Architrave.

          - Allows control of any devices part of the lighting control system.

          - Utilize RS485 wiring for low-voltage communication.

          - Functionality:

            - Upon button press, LEDs to immediately illuminate.

            - LEDs to reflect the true system status. LEDs to remain illuminated if the button press was properly processed or LEDs to turn off if the button press was not processed.

            - Allows for easy reprogramming without replacing unit.

            - Replacement of units does not require reprogramming.

          - Provide faceplates with concealed mounting hardware.

          - Engrave wall stations with button, zone, and scene descriptions to be selected by Architect or Owner.

          - Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

          - Software Configuration:

            - Customizable control station device button functionality:

              - Buttons can be programmed to perform single defined action.

              - Buttons can be programmed to perform defined action on press and defined action on release.

              - Buttons can be programmed using conditional logic off of a state variable such as time of day or partition status.

          - Control station device LEDs to support logic that defines when it is illuminated:

            - Scene logic (logic is true when all zones are at defined levels).

            - Room logic (logic is true when at least one zone is on).

            - Pathway (logic is true when at least one zone is on).

            - Last scene (logic is true when spaces are in defined scenes).

          - Contact Closure Interface: Accepts both momentary and maintained contact closures.

          - Provide integral infrared receiver for personal control where indicated.

        - Single-Scene or Zoned Wired Control:

          - Product: Pico Wired Control.

          - Turn an individual fixture or group of fixtures on and off.

          - Raise and lower light levels.

          - Recall favorite light levels.

        - Four-Button Preset Wallstation:

          - Product: EcoSystem CC-4BRL Four-Button Control.

          - Recall four scenes plus all on or all off for one group of fixtures.

          - Master raise/lower control for entire group of fixtures.

          - Integral IR receiver for personal control.

          - Immediate local LED response upon button activation to indicate that a system command has been requested.

        - Wired Keyswitch:

          - Product: QS Keyswitch.

          - Configuration:

            - Three position, momentary, center position key removal; Model QSWS2-KSI-3MOC.

            - Three position, maintained, center position key removal; Model QSWS2-KSI-3MAC.

            - Two position, maintained, center position key removal; Model QSWS2-KSI-2MAC.

            - Two position, maintained, any position key removal; Model QSWS2-KSI-2MAA.

          - Allows control of any devices part of the lighting control system.

          - Utilize RS485 wiring for low-voltage communication.

          - Functionality:

            - Allows for easy reprogramming without replacing unit.

            - Requires key insertion to activate actions.

          - Provide faceplates with concealed mounting hardware.

          - Engrave wall stations with button, zone, and scene descriptions to be selected by Architect or owner.

          - Silk-screened borders, logos, and graduations to use graphic process that chemically bonds graphics to faceplate, resistant to removal by scratching and cleaning.

          - Software Configuration:

            - Customizable control station device button functionality:

              - Key positions can be programmed to perform single defined action.

              - Key positions can be programmed using conditional logic off of a state variable such as time of day or partition status.

        - Slider Control:

          - Product: QS Slider Control.

          - Allows control of any lighting zone in the system via intuitive analog slider control.

          - Utilize RS485 wiring for low-voltage communication.

          - Available in 1 to 16 zone configurations.

          - Available with or without a take switch to activate the slider scene.

          - Optional keypad ganging.

          - Slider zones can be chained in partitioned spaces.

          - Provide faceplates with concealed mounting hardware.

          - Provide customizable engraving of faceplate to be selected by Architect or owner.

          - Functionality:

            - Full range dimming of individual zones or groups of zones.

            - Zone levels indicated by slider position.

            - Integrates with multi-scene wired control.

    - Wireless (Radio Frequency) Controls:

      - Product(s):

        - 2-Button Control; Pico Wireless Control Model PJ-2B.

          - Button Marking:  Light (text); Light (icons); Power (icons); As indicated on drawings.

        - 2-Button with Raise/Lower Control; Pico Wireless Control Model PJ-2BRL.

          - Button Marking:  Light (text); Light (icons); As indicated on drawings.

        - 3-Button Control; Lutron Pico Wireless Control Model PJ-3B.

          - Button Marking:  Light (text); Light (icons); As indicated on drawings.

        - 3-Button with Raise/Lower Control; Pico Wireless Control Model PJ-3BRL.

          - Button Marking:  Light (text); Light (icons); Shade (text); Shade (icons); Shade 1 (text); Shade 2 (text); Screen (text); Drapery (text); Drapery (icons); Blackout (text); Sheer (text); Blind (text); As indicated on drawings.

        - Single Pedestal; Lutron Pico Pedestal Model L-PED1.

        - Double Pedestal; Lutron Pico Pedestal Model L-PED2.

        - Triple Pedestal; Lutron Pico Pedestal Model L-PED3.

        - Quadruple Pedestal; Lutron Pico Pedestal Model L-PED4.

        - Screw Mounting Kit; Lutron Model PICO-SM-KIT.

        - Wallplate Adapter; Lutron Model PICO-WBX-ADAPT.

      - Quantity: As indicated on the drawings.

      - Communicates via radio frequency to compatible dimmers, switches, and plug-in modules.

      - Does not require external power packs, power or communication wiring.

      - Allows for easy reprogramming without replacing unit.

      - Button Programming:

        - Single action.

        - Toggle action.

        - Defined action on press and defined action on release.

      - Includes LED to indicate button press or programming mode status.

      - Models available with integral night light.

      - Mounting:

        - Capable of being mounted with a table stand or directly to a wall under a faceplate.

        - Faceplates: Provide concealed mounting hardware.

      - Power: Battery-operated with minimum ten-year battery life.

      - Finish: As specified for wall controls in "Device Finishes" under DIGITAL-NETWORK LIGHTING CONTROL SYSTEM - GENERAL REQUIREMENTS article above; White; Black; Ivory; Light Almond; White/Grey.

    - Infrared Handheld Controls:

      - Product(s):

        - Four-Scene Wireless Infrared Transmitter; Model GRX-IT-WH: Operates up to 50 feet (15 m) line-of-sight to receiver.

        - Single-Scene Wireless Infrared Transmitter; Model C-FLRC-WH: Operates up to 12 feet (3.7 m) line-of-sight to receiver.

      - Quantity: As indicated on the drawings.

      - Designed for use in conjunction with compatible infrared receiver and lighting control; compatibility dependent on that receiver, not transmitter.

      - Learnable by other variable frequency remote controls.

  - LOW-VOLTAGE CONTROL INTERFACES

    - Provide low-voltage control interfaces as indicated or as required to control the loads as indicated.

    - Connects to lighting management hub via RS485.

    - UL listed.

    - Contact Closure Interface:

      - Product: Model QSE-IO.

      - The contact closure input device to accept both momentary and maintained contact closures.

      - The contact closure output device can be configured for maintained or pulsed outputs.

      - Contact closure can be programmed using conditional logic off of a state variable such as time of day or partition status.

    - Wallbox Input Closure Interface:

      - Product: Model QSE-CI-WCI.

      - Mounts in wallbox behind contact closure keypad to provide interface for up to eight contact closure inputs.

      - The contact closure input device to accept both momentary and maintained contact closures.

    - RS232 and Ethernet Interface:

      - Product: Model QSE-CI-NWK-E.

      - Provide ability to communicate via Ethernet or RS232 to audiovisual equipment, touchscreens, etc.

      - Allow creation of custom output strings.

      - Provide control of:

        - Light scene selections.

        - Fine-tuning of light scene levels with raise/lower.

        - Shade group presets.

        - Fine-tuning of shade preset levels with raise/lower.

        - Simulate system wall station button presses and releases.

      - Provide status monitoring of:

        - Light scene status.

        - Shade group status.

        - Wall station button presses and releases.

        - Wall station LEDs.

      - Provide ability to send custom output strings.

    - DMX Interface:

      - Product: Model QSM-CI-DMX.

      - Provide ability to:

        - Map a single zone intensity to a single DMX512 lighting channel.

        - Map a single zone intensity to three DMX512 channels for RGB/CMY color control.

        - Map a single zone intensity to a single DMX512 integration channel.

        - Smoothly transition from one color to another in a cross fade.

        - Automatically sequence through a variety of colors.

        - Download, program, and customize a color wheel for each unit.

    - Sensor Modules:

      - Products:

        - Sensor module with both wired and wireless inputs; Model QSM2-4W-C.

        - Sensor module with wired inputs only; Model QSMX-4W-C.

        - Sensor module with wireless inputs only; Model QSM2-XW-C.

      - Wired Modules:

        - Provide wired inputs for:

          - Occupancy sensors.

          - Daylight sensors.

          - IR receivers for personal control.

          - Digital ballast wall stations.

      - Wireless Modules:

        - Provide wireless communication inputs for:

          - Occupancy sensors.

          - Daylight sensors.

          - Wireless controller.

        - RF Range: 30 feet (9 m) between sensor and compatible RF receiving devices.

        - RF Frequency: 434 MHz; operates in FCC governed frequency spectrum for periodic operation; continuous transmission spectrum is not permitted.

      - Communicate sensor information to wired low-voltage digital link for use by compatible devices.

  - WIRED SENSORS

    - Wired Occupancy Sensors:

      - General Requirements:

        - Connects directly to compatible ballasts and modules without the need of a power pack or other interface.

        - Turns off or reduces lighting automatically after reasonable time delay when a room or area is vacated by the last person to occupy the space.

        - Accommodates all conditions of space utilization and all irregular work hours and habits.

        - Comply with UL 94.

        - Self-Adaptive: Continually adjusts sensitivity and timing to ensure optimal lighting control for any use of the space.

        - Furnished with field-adjustable controls for time delay and sensitivity to override any adaptive features.

        - Provide capability to:

          - Add additional timeout system-wide without need to make local adjustment on sensor.

          - Group multiple sensors.

        - Power Failure Memory: Settings and learned parameters to be saved in non-volatile memory and not lost should power be interrupted and subsequently restored.

        - Furnished with all necessary mounting hardware and instructions.

        - Class 2 devices.

        - Ceiling-Mounted Sensors: Indicate viewing directions on mounting bracket.

        - Wall-Mounted Sensors: Provide swivel-mount base.

        - Color: White.

      - Wired Passive Infrared Sensors:

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

        - Ceiling-Mounted Sensors: Provide customizable mask to block off unwanted viewing areas.

        - Product(s):

          - Ceiling-Mounted Passive Infrared Sensor, 450 square feet ; Model LOS-CIR-450-WH: Coverage of 450 square feet  with ceiling height of 8 to 12 feet; 360 degree field of view.

          - Ceiling-Mounted Passive Infrared Sensor, 1500 square feet; Model LOS-CIR-1500-WH:  Coverage of 1500 square feet  with ceiling height of 8 to 12 feet; 360 degree field of view.

          - Wall-Mounted Passive Infrared Sensor; Model LOS-WIR-WH: Coverage of 1600 square feet  with ceiling height of 8 to 12 feet; 110 degree field of view.

      - Wired Ultrasonic Sensors:

        - Utilize an operating frequency of 32 kHz or 40 kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

        - Product(s):

          - Ceiling-Mounted Ultrasonic Sensor, 500 square feet; Model LOS-CUS-500-WH: Coverage of 500 square feet with ceiling height of 8 to 12 feet; 180 degree field of view.

          - Ceiling-Mounted Ultrasonic Sensor, 1000 square feet; Model LOS-CUS-1000-WH:  Coverage of 1,000 square feet with ceiling height of 8 to 12 feet; 180 degree field of view.

          - Ceiling-Mounted Ultrasonic Sensor, 2000 square feet; Model LOS-CUS-2000-WH: Coverage of 2000 square feet with ceiling height of 8 to 12 feet; 360 degree field of view.

      - Wired Dual Technology Sensors:

        - Passive Infrared: Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

        - Ultrasonic: Utilize an operating frequency of 32 kHz or 40 kHz, crystal-controlled to operate within plus/minus 0.005 percent tolerance.

        - Ceiling-Mounted Sensors: Provide customizable mask to block off unwanted viewing areas.

        - Isolated Relay: Provide an internal additional isolated relay with Normally Open, Normally Closed, and Common outputs for use with HVAC control, Data Logging and other control options where indicated.

        - Integral Photocell: Provide an integral photocell with adjustable sensitivity to prevent lights from turning on when there is sufficient natural light where indicated.

        - Product(s), Without Isolated Relay and Integral Photocell:

          - Ceiling-Mounted Dual Technology Sensor, 500 square feet; Model LOS-CDT-500-WH: Coverage of 500 square feet with ceiling height of 8 to 12 feet; 180 degree field of view.

          - Ceiling-Mounted Dual Technology Sensor, 1000 square feet ; Model LOS-CDT-1000-WH: Coverage of 1000 square feet with ceiling height of 8 to 12 feet ; 180 degree field of view.

          - Ceiling-Mounted Dual Technology Sensor, 2000 square feet; Model LOS-CDT-2000-WH: Coverage of 2000 square feet with ceiling height of 8 to 12 feet; 360 degree field of view.

          - Wall-Mounted Dual Technology Sensor; Model LOS-WDT-WH; Coverage of 1600 square feet with ceiling height of 8 to 12 feet; 110 degree field of view.

        - Product(s), With Isolated Relay and Integral Photocell:

          - Ceiling-Mounted Dual Technology Sensor, 500 square feet; Model LOS-CDT-500R-WH: Coverage of 500 square feet with ceiling height of 8 to 12 feet; 180 degree field of view; with isolated relay and integral photocell.

          - Ceiling-Mounted Dual Technology Sensor, 1000 square feet ; Model LOS-CDT-1000R-WH: Coverage of 1000 square feet with ceiling height of 8 to 12 feet; 180 degree field of view; with isolated relay and integral photocell.

          - Ceiling-Mounted Dual Technology Sensor, 2000 square feet; Model LOS-CDT-2000R-WH: Coverage of 2000 square feet with ceiling height of 8 to 12 feet; 360 degree field of view; with isolated relay and integral photocell.

          - Wall-Mounted Dual Technology Sensor; Model LOS-WDT-R-WH: Coverage of 1600 square feet with ceiling height of 8 to 12 feet; 110 degree field of view; with isolated relay and integral photocell.

    - Sensor Power Packs:

      - Product(s):

        - Model PP-DV Power Pack; 120-277 VAC power input/24 VDC, 100 mA power output.

        - Model PP-DV-M Power Pack; 120-277 VAC power input (manual)/24 VDC, 100 mA power output.

      - Provide sensor power packs where required for power connection to sensors.

      - For ease of mounting, installation and future service, power pack(s) to be able to mount through a 1/2 inch knockout in a standard electrical enclosure and be an integrated, self-contained unit consisting internally of an isolated load switching control relay and a transformer to provide low-voltage power. Transformer to provide power to a minimum of three sensors.

      - Relay Contact Rating: 20 A ballast (120/277 V); 15 A incandescent (120 V).

      - Plenum-rated.

      - Control Wiring Between Sensors and Control Units: Class 2, 18-24 AWG, stranded UL Classified, PVC insulated or TEFLON jacketed cable suitable for use in plenums, where applicable.

    - Infrared Receivers:

      - Product: Model EC-IR-WH.

      - Use Class 2 wiring for low voltage communication.

      - Can be replaced without reprogramming.

      - 360 degree reception of wireless infrared remote controls.

      - Immediate local LED response upon reception of handheld transmitter communication.

      - Mountable on lighting fixtures or recessed acoustical ceiling tiles.

      - Constructed via sonic welding.

      - Color: White.

    - Wired Daylight Sensors:

      - Digital Interior Daylight Sensor:

        - Product: Model EC-DIR-WH.

        - Use Class 2 wiring for low voltage communication.

        - Can be replaced without reprogramming.

        - Open-loop basis for daylight sensor control scheme.

        - Stable output over temperature from 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C).

        - Partially shielded for accurate detection of available daylight to prevent fixture lighting and horizontal light component from skewing sensor detection.

        - Provide linear response from 0 to 500 footcandles.

        - Integral IR receiver for personal control.

        - Mountable on lighting fixtures or recessed acoustical ceiling tiles.

        - Constructed via sonic welding.

        - Color: White.

      - Daylight Control Package:

        - Product: CES Series (CES Analog Sensor, LC8 Controller, and Power Pack).

        - Controller:

          - Product: Model LC8.

          - Automatically switches a dry contact according to changes in ambient light levels.

          - Fully adjustable separate high and low setpoints, with an adjustable dead band between set points to prevent unwanted cycling.

          - Input time delay to prevent unwanted cycling due to intermittent light level fluctuations.

          - Signal/setpoint and relay status indication.

          - Sensor calibration input.

        - Sensors:

          - Class 2, three-wire analog devices.

          - Provision for zero or offset based signal.

          - Indoor Photo Sensors; Model CES/I: With fresnel lens and 60 degree cone of response; sensor range of 0 to 750 footcandles.

          - Outdoor Photo Sensors; Model CES/O: Weatherproof, with hood over aperture to shield sensor from direct sunlight; sensor range of 0 to 750 footcandles.

          - Atrium Photo Sensors; Model CES/A: With translucent dome and 180 degree field of view; sensor range of 2 to 2,500 footcandles.

          - Skylight Photo Sensors; Model CES/S: With translucent dome and 180 degree field of view; sensor range of 10 to 7,500 footcandles.

    - Infrared Partition Sensors:

      - Product: Model GRX-IRPS-WH.

      - Provide contact closure based on status of the partition wall (open/close) enabling automatic linking of controls.

  - WIRELESS SENSORS

    - General Requirements:

      - Operational life of 10 years without the need to replace batteries when installed per manufacturer's instructions.

      - Communicates directly to compatible RF receiving devices through use of a radio frequency communications link.

      - Does not require external power packs, power wiring, or communication wiring.

      - Capable of being placed in test mode to verify correct operation from the face of the unit.

      - RF Range: 30 feet (9 m) between sensor and compatible RF receiving device(s).

      - Electromagnetic Interference/Radio Frequency Interference (EMI/RFI) Limits: Comply with FCC requirements of CFR, Title 47, Part 15, for Class B application.

    - Wireless Occupancy/Vacancy Sensors:

      - General Requirements:

        - Provides a clearly visible method of indication to verify that motion is being detected during testing and that the unit is communicating to compatible RF receiving devices.

        - Utilize multiple segmented lens, with internal grooves to eliminate dust and residue build-up.

        - Sensing Mechanism: Passive infrared coupled with technology for sensing fine motions; XCT Technology. Signal processing technology detects fine-motion passive infrared (PIR) signals without the need to change the sensor's sensitivity threshold.

        - Provide optional, readily accessible, user-adjustable controls for timeout, automatic/manual-on, and sensitivity.

        - Turns off lighting after reasonable and adjustable time delay once the last person to occupy the space vacates a room or area. Provide adjustable timeout settings of 1, 5, 15, and 30 minutes.

        - Capable of turning dimmer's lighting load on to an optional locked preset level selectable by the user. Locked preset range to be selectable on the dimmer from 1 percent to 100 percent.

        - Color: White.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

        - Sensor lens to illuminate during test mode when motion is detected to allow installer to verify coverage prior to permanent mounting.

        - Ceiling-Mounted Sensors:

          - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

          - Provide recessed mounting bracket compatible with drywall and compressed fiber ceilings.

          - Provide customizable mask to block off unwanted viewing areas.

        - Wall-Mounted Sensors: Provide wall or corner mounting brackets compatible with drywall and plaster walls.

      - Wireless Combination Occupancy/Vacancy Sensors:

        - Wall-Mounted Sensors: Programmable to operate as an occupancy sensor (automatic-on and automatic-off), or a vacancy sensor (manual-on and automatic-off).

        - Product(s):

          - Ceiling-Mounted Occupancy/Vacancy Sensor; Radio Powr Savr Series, Model LFR2-OCR2B-P-WH: Coverage from 324 square feet to 676 square feet depending on ceiling height from 8 to 12 feet; 360 degree field of view.

          - Wall-Mounted Occupancy/Vacancy Sensor; Radio Powr Savr Series, Model LFR2-OWLB-P-WH: Minor motion coverage of 1500 square feet and major motion coverage of 3000 square feet with mounting height of 6 to 8 feet; 180 degree field of view.

          - Corner-Mounted Occupancy/Vacancy Sensor; Radio Powr Savr Series, Model LFR2-OKLB-P-WH: Minor motion coverage of 1225 square feet and major motion coverage of 2500 square feet with mounting height of 6 to 8 feet; 90 degree field of view.

          - Hallway Occupancy/Vacancy Sensor; Radio Powr Savr Series, Model LFR2-OHLB-P-WH: Major motion coverage of up to 150 feet with mounting height of 6 to 8 feet; narrow field of view.

      - Wireless Vacancy-Only Sensors:

        - Operates only as a vacancy sensor (manual-on and automatic-off).

        - Product(s):

          - Ceiling-Mounted Vacancy-Only Sensor; Radio Powr Savr Series, Model LFR2-VCR2B-P-WH: Coverage from 324 square feet to 676 square feet depending on ceiling height from 8 to 12 feet; 360 degree field of view.

          - Wall-Mounted Vacancy-Only Sensor; Radio Powr Savr Series, Model LFR2-VWLB-P-WH: Minor motion coverage of 1500 square feet and major motion coverage of 3000 square feet with mounting height of 6 to 8 feet; 180 degree field of view.

          - Corner-Mounted Vacancy-Only Sensor; Radio Powr Savr Series, Model LFR2-VKLB-P-WH: Minor motion coverage of 1225 square feet and major motion coverage of 2500 square feet with mounting height of 6 to 8 feet; 90 degree field of view.

          - Hallway Vacancy-Only Sensor; Radio Powr Savr Series, Model LFR2-VHLB-P-WH: Major motion coverage of up to 150 feet with mounting height of 6 to 8 feet; narrow field of view.

    - Wireless Daylight Sensors:

      - Product: Model LFR2-DCRB.

      - Open-loop basis for daylight sensor control scheme.

      - Stable output over temperature from 32 degrees F (0 degrees C) to 104 degrees F (40 degrees C).

      - Partially shielded for accurate detection of available daylight to prevent fixture lighting and horizontal light component from skewing sensor detection.

      - Provide linear response from 0 to 10,000 footcandles.

      - Color: White.

      - Mounting:

        - Provide surface mounting bracket compatible with drywall, plaster, wood, concrete, and compressed fiber ceilings.

        - Provide all necessary mounting hardware and instructions for both temporary and permanent mounting.

        - Provide temporary mounting means to allow user to check proper performance and relocate as needed before permanently mounting sensor. Temporary mounting method to be design for easy, damage-free removal.

  - ACCESSORIES

    - Emergency Lighting Interface:

      - Product: Model LUT-ELI.

      - Provides total system listing to UL 924 when used with lighting control system.

      - Senses all three phases of building power.

      - Provides an output to power panels or digital ballast interfaces if power on any phase fails and sends all lights controlled by these devices to 100 percent intensity. Lights to return to their previous intensities when normal power is restored.

      - Accepts a contact closure input from a fire alarm control panel.

    - Provide power supplies as indicated or as required to power system devices and accessories.

      - Product(s):

        - Junction box-mounted power supply for shades, keypads, and accessories, and for providing additional low voltage power to communication link; Model QSPS-J-1-50; with miswire and thermal protection.

        - Plug-in power supply for shades, drapery drive units, keypads, and accessories, and for providing additional low voltage power to communication link; Model QSPS-P1-1-50; with miswire protection; powered from standard receptacle using cord 6 feet in length.

        - Ten output power supply panel for shades, drapery drive units, keypads and accessories, and for providing additional low voltage power to communication link; Model QSPS-P1-10-60.

        - Power supply for keypads and accessories (not for shades/window treatments), and for providing additional low voltage power to communication link; Model STEP-PS.

  - SOURCE QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Factory Testing; Standard Factory Testing:

      - Perform full-function factory testing on all completed assemblies. Statistical sampling is not acceptable.

      - Perform full-function factory testing on 100 percent of all ballasts and LED drivers.

      - Perform factory audit burn-in of all dimming assemblies and panels at 104 degrees F (40 degrees C) at full load for two hours.

      - Perform factory burn-in of 100 percent of all ballasts at 104 degrees F (40 degrees C).

- EXECUTION

  - EXAMINATION

    - Verify that field measurements are as shown on the drawings.

    - Verify that ratings and configurations of system components are consistent with the indicated requirements.

    - Verify that mounting surfaces are ready to receive system components.

    - Verify that conditions are satisfactory for installation prior to starting work.

  - INSTALLATION

    - Perform work in a neat and workmanlike manner in accordance with NECA 1 and, where applicable, NECA 130.

    - Install products in accordance with manufacturer's instructions.

    - Provide dedicated network between lighting management system computer and lighting management hubs.

    - Define each dimmer/relay load type, assign each load to a zone, and set control functions.

    - Sensor Layout and Tuning:  Include additional costs for Lighting Control Manufacturer's Sensor Layout and Tuning service; LSC-SENS-LT:

      - Lighting Control Manufacturer to take full responsibility for wired or wireless sensor layout and performance for sensors provided by Lighting Control Manufacturer.

      - Lighting Control Manufacturer to analyze the reflected ceiling plans, via supplied electronic AutoCAD format, and design a detailed sensor layout that provides adequate occupancy sensor coverage and ensures occupancy and daylight sensor performance per agreed upon sequence of operations. Contractor to utilize the layouts for sensor placement.

      - During startup, Lighting Control Manufacturer to direct Contractor regarding sensor relocation, as required, should conditions require a deviation from locations specified in the drawings.

      - Lighting Control Manufacturer to provide up to two additional post-startup on-site service visits within one calendar year from Date of Substantial Completion to fine-tune sensor calibration per the agreed upon sequence of operations.

    - Mount exterior daylight sensors to point due north with constant view of daylight.

    - Ensure that daylight sensor placement minimizes sensor view of electric light sources. Locate ceiling-mounted and luminaire-mounted daylight sensors to avoid direct view of luminaires.

    - Automated Shade Control Sensors:

      - Mount rooftop cloudy day sensors to point in the direction of each facade.

      - Ensure that window shadow sensor placement provides an unobstructed view of outdoors. Do not place at a skylight or above indirect luminaires.

    - Lamp Burn-In: Operate lamps at full output for prescribed period per manufacturer's recommendations prior to use with any dimming controls. Replace lamps that fail prematurely due to improper lamp burn-in.

    - Lamp Lead Lengths: Do not exceed 3 feet for T4 4-pin compact and T5 BIAX lamps and 7 feet for T5, T5-HO, T8 U-bend, and T8 linear fluorescent lamps.

    - LED Light Engine/Array Lead Length: Do not exceed 100 feet.

    - System and Network Integration Consultation; LSC-INT-VISIT: Include additional costs for Lighting Control Manufacturer to conduct meeting with facility representative and other related equipment manufacturers to discuss equipment and integration procedures.

      - Coordinate scheduling of visit with Lighting Control Manufacturer. Manufacturer recommends that this visit be scheduled early in construction phase, after system purchase but prior to system installation.

    - Identify system components in accordance with Section 26 0553.

  - FIELD QUALITY CONTROL

    - See Section 01 4000 - Quality Requirements, for additional requirements.

    - Manufacturer's Startup Services; Standard Startup Services:

      - Manufacturer's authorized Service Representative to conduct minimum of two site visits to ensure proper system installation and operation.

      - Conduct Pre-Installation visit to review requirements with installer as specified in Part 1 under "Administrative Requirements".

      - Conduct second site visit upon completion of lighting control system to perform system startup and verify proper operation:

        - Verify connection of power wiring and load circuits.

        - Verify connection and location of controls.

        - Energize lighting management hubs and download system data program.

        - Address devices.

        - Verify proper connection of panel links (low voltage/data) and address panel.

        - Download system panel data to dimming/switching panels.

        - Check dimming panel load types and currents and supervise removal of by-pass jumpers.

        - Verify system operation control by control.

        - Verify proper operation of manufacturer's interfacing equipment.

        - Verify proper operation of manufacturer's supplied PC and installed programs.

        - Configure initial groupings of ballast for wall controls, daylight sensors and occupancy sensors.

        - Provide initial rough calibration of sensors; fine-tuning of sensors is responsibility of Contractor.

        - Train Owner's representative on system capabilities, operation, and maintenance, as specified in Part 3 under "Closeout Activities".

        - Obtain sign-off on system functions.

        - After Hours Startup; LSC-AH-SU: Include additional costs to perform manufacturer's startup procedures outside normal working hours (Monday through Friday, 7am to 5pm).

    - Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

  - ADJUSTING

    - On-Site Scene and Level Tuning; LSC-AF-VISIT: Include additional costs for Lighting Control Manufacturer to visit site to conduct meeting with Engineer; Owner's representative; Lighting Designer to make required lighting adjustments to the system for conformance with original design intent.

  - CLEANING

    - Clean exposed surfaces to remove dirt, paint, or other foreign material and restore to match original factory finish.

  - COMMISSIONING

    - See Section 01 9113 for commissioning requirements.

  - CLOSEOUT ACTIVITIES

    - See Section 01 7800 - Closeout Submittals, for closeout submittals.

    - See Section 01 7900 - Demonstration and Training, for additional requirements.

    - Demonstration:

      - On-Site Performance-Verification Walkthrough; Lutron LSC-WALK: Include additional costs for lighting control manufacturer to provide on-site demonstration of system functionality to commissioning agent; facility representative; or Engineer.

    - Training:

      - Include services of manufacturer's authorized Service Representative to perform on-site training of Owner's personnel on operation, adjustment, and maintenance of lighting control system as part of standard system start-up services.

        - Include training on software to be provided:

          - Configuration software used to make system programming and configuration changes.

          - Control and monitor.

          - Energy savings display software.

          - Personal web-based control software.

      - Customer-Site Solution Training Visit; LSC-TRAINING: Include additional costs for Lighting Control Manufacturer to provide one day of additional on-site system training.

  - PROTECTION

    - Protect installed products from subsequent construction operations.

  - MAINTENANCE

    - See Section 01 7000 - Execution Requirements, for additional requirements relating to maintenance service.

    - Software Maintenance Agreement; LSC-SMA: Include additional costs for manufacturer to provide quarterly compatibility testing results for PC-based lighting control software and new patches issued for Microsoft Operating System, Database, and Browser tools.

      - If new Microsoft patches create a software conflict, manufacturer to provide lighting control software patches to ensure continued operation.

    - System Optimization Visit; LSC-SYSOPT: Include additional costs for Lighting Control System Manufacturer to visit site six months after system start-up to evaluate system usage and discuss opportunities to make efficiency improvements that will fit with the current use of the facility.

END OF SECTION