# SECTION 265113

# INTERIOR LIGHTING FIXTURES, LAMPS, AND BALLASTS

- GENERAL

SUMMARY

Section Includes:

Fluorescent Electronic dimming ballast.

Related Sections:

Section 262726 - Wiring Devices: Dimmers

Section 260923 – Lighting Control Devices: Occupancy sensors

REFERENCES

American National Standards Institute / Institute of Electrical and Electronic Engineers (ANSI/IEEE):

C62.41-1991 – Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

International Organization for Standardization (ISO):

9001 (2008) – Quality Management Systems.

National Electrical Manufacturers Association (NEMA):

WD1 (R2005) - General Color Requirements for Wiring Devices.

Ballast standards

Underwriters Laboratories, Inc. (UL):

935 (2005) - Fluorescent Ballasts

DESCRIPTION

Electronic dimming ballast.

3-Wire (Line Voltage Controlled) Dimming Ballasts

2-Wire (Line Voltage Controlled) Dimming Ballasts

0-10 V (Low Voltage Controlled) Dimming Ballasts

Digital (Low Voltage Controlled) Dimming Ballasts

SUBMITTALS

Submit under provisions of Section 013300.

Specification Conformance Document:  Indicate whether the submitted equipment:

Meets specification exactly as stated.

Meets specification via an alternate means and indicate the specific methodology used.

Product Data: Catalog cut sheets with performance specifications demonstrating compliance with specified requirements.

QUALITY ASSURANCE

Manufacturer: Minimum 10 years of experience in manufacture of electronic dimming ballasts.

Manufacturer’s Quality System: Registered to ISO 9001:2008 Quality Standards, including in-house engineering for product design activities.

Listed by UL. Provide evidence of compliance upon request.

PROJECT CONDITIONS

Do not install equipment until following conditions can be maintained in spaces to receive equipment:

Ambient temperature: 10 degrees to 60 degrees C (50 degrees to 140 degrees F).

Relative humidity: Maximum 90 percent, non-condensing.

Protected from dust and excess moisture during installation.

WARRANTY

Provide manufacturer’s warranty covering 3 years or 5 years with factory commissioning (part of a system) on ballasts from date of purchase.

MAINTENANCE

Make ordering of new equipment for expansions, replacements, and spare parts available to end user twenty-four hours a day, seven days a week.

Make replacements available for minimum of ten years from date of manufacture.

- PRODUCTS

MANUFACTURERS

Basis of design product: Lutron or subject to compliance and prior approval with specified requirements of this section, one of the following:]

<Insert manufacturer’s name>

Substitutions: Under provisions of Division 1.

All proposed substitutions (clearly delineated as such) must be submitted in writing for approval by the design professional a minimum of 10 working days prior to the bid date and must be made available to all bidders.

Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.

Provide complete engineered shop drawings (including power wiring) with deviations for the original design highlighted in an alternate color to the engineer for review and approval prior to rough-in.

GENERAL

Ten-year operational life while operating with a case temperature range of 10 degrees C (50 degrees F) to 75 degrees C (167 degrees F) and 90 percent non-condensing relative humidity.

Designed and tested to withstand electrostatic discharges up to 15,000 V without impairment per IEC 801-2.

Electrolytic capacitors to operate at least 20 degrees C below the capacitor’s maximum temperature rating when the ballast is under fully-loaded conditions and case temperature is 75 degrees C (167 degrees F).

Programmed Rapid Start Type.

Current crest factor (CCF) less than 1.7.

Meet ANSI C82.11 High frequency ballast standard.

Will not interfere with infrared devices operating at frequencies between 38 kHz and 42 kHz.

Withstand up to a 4,000 volt surge without impairment of performance as defined by ANSI C62.41 Category A.

Manufactured in a facility that employ ESD reduction practices in compliance with ANSI/ESD S20.20.

Inaudible in a 27 dBA ambient.

No visible change in light output with a variation of +/- 10 percent line voltage input.

Total Harmonic Distortion less than 20 percent and meet ANSI C82.11 maximum allowable THD requirements

Actively prevent overheating in T5-HO linear fluorescent lamp applications.

Ballasts to track evenly across:

Multiple lamp lengths.

All light levels.

3-Wire Control

Continuous dimming from 100 percent to 10 percent: Lutron EcoSystem, 5 percent:  Lutron EcoSystem for T4, 5 percent: Lutron Hi-lume 3D for T5 Twin-Tube, 1 percent: Lutron Hi-lume, 1 percent for EcoSystem H-Series, 1 percent or better: Lutron Hi-lume 3D relative light output.

Provide integral fault protection to prevent ballast failure in the event of a mis-wire.

Maximum inrush current of 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

Lutron Tu-wire: 2-Wire control

Continuous dimming from 100 percent to 5 percent relative light output.

Maximum inrush current of 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

Lutron EcoSystem: Digital Control

Continuous dimming from 100 percent to 10 percent relative light output for T8 U-bend and linear fluorescent lamps, 10 percent for T5 or T5-HO linear fluorescent lamps.

Connect without interface to:

Occupant sensor (motion detector).

Daylight sensor.

Personal control input (keypad or infrared receiver).

Provide a 20VDC source to power connected sensors.

Generate digital communication commands to distribute ballast and sensor data on the digital bus.

Monitor and report lamp and ballast status.

Lights automatically return to the setting prior to power interruption.

Each ballast responds independently to:

Up to 32 occupant sensors.

Up to 64 personal control inputs.

Up to 2 daylight sensors.

Unique internal reference number visibly displayed on ballast cover.

Averages 2 independent daylight harvesting inputs internally.

Responds to digital load shed command.

Sets high end trim.

Automatically scales light output proportional to load shed command.

Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by 3 percent to 27 percent.

Maximum inrush current of 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

Lutron EcoSystem FOR T4 COMPACT FLUORESCENT LAMPS: Digital Control

Continuous dimming from 100 percent to 5 percent relative light output for T4 compact and T5 twin tube lamps.

Generate digital communication commands to distribute ballast data on the digital bus.

Monitor and report lamp and ballast status.

Lights automatically return to the setting prior to power interruption.

Each ballast responds independently to:

Up to 32 occupant sensors.

Up to 64 personal control inputs.

Up to 2 daylight sensors.

Unique internal reference number visibly displayed on ballast cover.

Averages 2 independent daylight harvesting inputs internally.

Responds to digital load shed command.

Sets high end trim.

Automatically scales light output proportional to load shed command.

Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by 3 percent to 27 percent.

Maximum inrush current of 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

Lutron ecosystem H-series: Digital Control

Continuous dimming from 100 percent to 0.7 percent relative light output, at 1.17BF or 0.85 percent relative light output, at 1.0 BF for T8 U-bend and linear fluorescent lamps. 1.0 percent relative light output, at 1.0 BF for T5 and T5-HO lamps.

Monitor and report lamp and ballast status.

Lights automatically return to the setting prior to power interruption.

Each ballast responds independently to:

Up to 32 occupant sensors.

Up to 64 personal control inputs.

Up to 2 daylight sensors.

Unique internal reference number visibly displayed on ballast cover.

Averages 2 independent daylight harvesting inputs internally.

Responds to digital load shed command.

Sets high end trim.

Automatically scales light output proportional to load shed command.

Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by 3 percent to 27 percent.

Generate digital communication commands to distribute ballast data on the digital bus.

Lutron Hi-lume 3D: Digital Control

Continuous dimming from 100 percent to 0.7 percent relative light output, at 1.17BF or 0.85 percent relative light output, at 1.0 BF for T8 U-bend and linear fluorescent lamps. 1.0 percent relative light output, at 1.0 BF for T5 and T5-HO lamps.  5.0 percent relative light output, at 1.0 BF for T5 Twin-Tube lamps.

Monitor and report lamp and ballast status.

Lights automatically return to the setting prior to power interruption.

Each ballast responds independently to:

Up to 32 occupant sensors.

Up to 64 personal control inputs.

Up to 2 daylight sensors.

Unique internal reference number visibly displayed on ballast cover.

Averages 2 independent daylight harvesting inputs internally.

Responds to digital load shed command.

Sets high end trim.

Automatically scales light output proportional to load shed command.

Example: If light output is at 30 percent and a load shed command of 10 percent is received, the ballast automatically sets the maximum light output at 90 percent and lowers current light output by 3 percent to 27 percent.

Generate digital communication commands to distribute ballast data on the digital bus.

Maximum inrush current of 7 amperes for 120V ballasts and 3 amperes for 277V ballasts.

SOURCE QUALITY CONTROL

Perform full-function testing on 100 percent of all ballasts at the factory.

Perform burn-in at 40 degrees C (104 degrees F) ambient temperature on 100 percent of all ballasts at the factory.

- EXECUTION

INSTALLATION

Install equipment in accordance with manufacturer’s installation instructions.

Provide complete installation of system in accordance with Contract Documents.

Season lamps at full intensity according to lamp manufacturer’s recommendation.

Lead lengths to lamp sockets not to exceed three feet (.9m) for T4 4-pin compact lamps and T5 Twin-Tube and seven feet (2.1 m) for T5, T5-HO, T8 U-bend, and T8 linear fluorescent lamps.

Rapid starts sockets must meet IEC 60400

END OF SECTION