SECTION 263600

EMERGENCY POWER CONTROL (EPC)/AUTOMATIC LOAD CONTROL RELAY (ALCR)

- - electrical specifications

  - The EPC shall automatically illuminate connected emergency loads upon utility power interruption, regardless of room switch position. (NEC 700.24)

  - The EPC shall include an automatic diagnostic which is initiated when the room switch is turned off.  This test procedure will turn the emergency luminaires on for at least 2 seconds, indicating that an emergency power source is available & that the device, ballast, & lamp are all functioning correctly.

  - Automatic diagnostic shall be approved to meet periodic testing requirements (NEC 700.3 NFPA 101 7.9.3)

  - Local room switch or lighting control shall turn both regular & emergency luminaires on at the same time (no dedicated emergency room switch required).

  - The EPC shall have a minimum load rating of 20 Amps at 120V or 277V , 1800W Tungsten at 120V & 1500W Tungsten at 277V, 1 HP, General Use 20 Amps.

  - The EPC shall accept 120V & 277V 60 Hz Input & Output (voltage tolerance +/- 15%).

  - The EPC shall include emergency power and regular power indicator LED’s and a manual test switch which are visible to room occupants when installed flush. (UL924 Section 29)

  - The EPC shall accept separate phases on the constant hot & switched hot inputs.

  - The EPC shall include high voltage input surge protection up to 50,000V.

  - Load contacts shall be able to withstand 10 direct shorts while connected to 20 Amp breaker without permanent damage.

  - The EPC shall not generate any objectionable electrical or mechanical noise.

- – MECHANICAL SPECIFICATIONS

  - The EPC shall mount inside a 4-11/16” junction box with an extension & single gang plaster ring.

  - The EPC shall be installed flush to the ceiling so that test switch & led’s are in plain view of room occupants as required by some local electrical codes.

  - The EPC shall have UL94-V0 or UL94-5VA flame rating & be approved for installation above the suspended ceiling

  - Enclosure shall be white

  - Dimensions: Flush plate:  4-3/4” x 2-3/4” x 1/4” recessed body: 2-7/8” x 1-3/4” x 1-3/4”

- - General Specifications

  - The EPC-D shall be UL924 listed.

  - Warranty shall be 5 year replacement warranty

  - The EPC- shall comply with all applicable N.E.C., N.F.P.A, OSHA, & local safety codes.

  - Models EPC-1 by LVS, Inc. 800-982-4587  www.lvscontrols.com.