SECTION 263600

EMERGENCY POWER CONTROL FOR DIMMABLE EMERGENCY FIXTURES

- Electrical Specifications

  - The EPC-D shall automatically illuminate connected emergency loads to full brightness upon utility power interruption, regardless of switch/dimmer position. (NEC 700.24)

  - The EPC-D shall be compatible with 2-wire, 3-wire, 0-10V, & DALI/EcoSystem dimming systems & ballasts.

  - The same local room switch, dimmer, or lighting control shall dim both regular & emergency luminaires at the same level during normal operation.

  - The EPC-D shall have a minimum load rating of 20 Amps at 120V or 277V , 1800W Tungsten at 120V

  - The EPC-D shall accept (120 or 277V) 60Hz Input & Output (voltage tolerance +/- 15%).

  - The EPC-D shall include emergency power & regular power indicator LED’s & a manual test switch which are visible to room occupants when installed flush. (UL924 Section 29)

  - The EPC-D shall accept separate phases on the regular hot , emergency hot, and dimmed hot inputs.

  - The EPC-D shall include high voltage input surge protection up to 50,000V.

  - Load contacts shall be able to withstand 10 direct shorts while connected to 20 Amp breaker without permanent damage.

  - The EPC-D shall not generate any objectionable electrical or mechanical noise.

- Mechanical Specifications

The EPC-D shall mount inside a 4-11/16” junction box with an extension & double gang plaster ring.

The EPC-D shall be installed flush to the ceiling so that test switch & LED’s are in plain view of room occupants as required by some local electrical codes.

The EPC-D shall have UL94-V0 or UL94-5VA flame rating & be approved for installation above the suspended ceiling

Enclosure shall be white

Dimensions:  Flush mounted size: 6” x 6” x 1/4”  body size: 4-1/4” x 4-1/4” x 1-1/2”

- General Specifications

The EPC-D shall be UL924 listed.

Warranty shall be 5 year replacement warranty

The EPC-D shall comply with all applicable N.E.C., N.F.P.A, OSHA, & local safety codes.

Models EPC-D-F-120 or EPC-D-F -277 by LVS, Inc. 800-982-4587  www.lvscontrols.com.